225 MWe Combined Cycle Plant (First Phase)

Purchase and Relocation

PREAMBLE

This Combined Cycle power plant description document is ‘still work in progress’.  (See Annexure ‘Pending Information’)

All the technical data that is necessary to carry out a full evaluation and potential of the asset, as-is, has not yet been received from the current owner.

The receipt of information is slow and is dependent on the rate at which it can be retrieved from the mass of original project documentation, equipment specifications and drawings.

The plant, as described herein, is to be sold as-is.

Important

This document is intended to serve only as a guide for preliminary evaluation by the potential project developer and his engineer, and nothing within this document should be construed at this stage as a contractual or commercial commitment without the exchange of appropriate agreements.

INTRODUCTION

The powerplant was designed for local site conditions in India as a base load combined cycle with 225 MW nominal capacity constructed in a 1st phase and with intention to add an additional 133 MW as a 2nd phase expansion.

The 1st phase natural gas-fired plant described below has its equipment already 95% (by value) constructed. However, it has never been commissioned due to lack of availability of natural gas.  Construction stopped in 2017. All installed equipment is still 100% unused and uncommissioned.  The power plant remained uncompleted to this day due to inability of the state to provide the site with natural gas.

It is proposed that the plant be sold for dismantling and re-location.

Consulting Engineers

The project’s consulting engineer was one of the world’s leading independent engineering consultancy and project management Groups.

Dismantling and Relocation

It is proposed that the existing equipment be sold to a new Owner - Operator

- to be totally dismantled, relocated and installed on a new site as a fully operational combined cycle power plant, with modifications to optimize performance.

- The existing plant, as-is, should be dismantled under buyer’s supervision and in a controlled logical manner to facilitate equipment inspection during dismantling to minimizing damage and losses.  Packaging and expediting should, as far as possible, be carried out in a sequence to minimize storage and to facilitate erection at the new site.

- The plant layout has been established and savings in design/engineering for relocating the plant may be achieved by retaining the current layout as mush as possible

Advantages

- The power plant has been fully engineered and all plant’s main units are compatible with the original design and operational objective.

- The Frame 6111+e gas turbines are designed for extended intervals between inspections and major overhauls.

- The supplier of the main plant and equipment is GE (General Electric) and a manufacturer’s performance warranty can be re-validated.

- Installation time for the relocated plant can be reduced by about 50% compared to newly ordered equipment and grass-roots design

- Overall CAPEX for the relocated plant can be reduced by 50% with respect to a new grass-roots project.

- combined cycle plant 1st phase has an ISO fuel efficiency of approximately 54% at MCR capacity. (2nd Phase not yet installed)

- Implementation of the 100 MW expansion in phase II by installing high efficiency aeroderivatives will mitigate the combined cycle short-comings during variable load operation.

Disadvantages

- For maximum economic benefit, the plant should operate at MCR as much as possible. The design of the plant does not lend itself to load-following or stop-start operation and, with respect to increased renewables energy being admitted into the European grid, ways of increasing the plant’s operational flexibility should be examined.

- Phase 2 would make provision for open-cycle aeroderivatives that have the ability to operate continuously at variable load and with multiple stop-starts and without any deleterious effects on performance, plant longevity or significant plant de-rating. Phase 2, would have the capacity to better ensure the efficiency of the phase 1 combined cycle operation.

- The original project design-point parameters are not yet known and so the off-design performance has not yet been determined. However, the cost of the much-diminished CAPEX together with good overall efficiency, may compensate for the lower capacity yield at site conditions.

- Apart from some lack of operational flexibility, this plant does not represent the latest technology, and this is reflected in the plant ISO efficiency of 54%. However, the technology is extremely well-proven and extremely reliable from past experience and may well be more advantageous than a more recent technology from a profitability aspect, given the present low cost of money and low price of fuel and expected low Capex.

Caveat

The operating regime of the plant after relocation is not yet known, but once disclosed, this is likely to impact certain plant design elements, and these may affect overall plant performance at the new site.

MAIN EQUIPMENT and Balance of Plant (BoP)

Main Equipment Groups (ISBL)

The main equipment of the 1st phase construction comprises:

- 2	77 MWe GE F6FA+e gas turbine generators (Mark VI control)

- 2	Generators, 95 MVA

- 1	74 MW GE Steam Turbine

- 2	Dual pressure HRSG with deaerators and feed pumps

- 1	Air-cooled steam condenser (ACC) by GEA

- 1	Water purification/demineralizing plant

- 1	Incoming Fuel gas conditioning and metering skid

- 2 	Gas turbine fuel gas conditioning and metering skids

Balance of Plant (ISBL)

The balance of plant (BoP) consists of, but is not limited to:

- Switch yard with step-up transformers MV, HV for grid connection

- Station transformers, MV, LV switchgear

- Effluent treatment plant

- Fin-Fan coolers (for lube-oil and alternator cooling)

- HV, MV and

- Distributed control system and UPS (uninterrupted power supply)

- Fire water and CO2 fire-protection system (Agnice)

- 500 kW black-start diesel generator

- Fuel Gas conditioning skid, oner per gas turbine

- Compressed Air System (Atlas Copco)

- Cooling water system

- Hot stacks with diverters

- Main cabling

- Generator circuit breakers (GCB) ABB

- Laboratory equipment

- Steam piping and instrumentation (not fully connected)

- Boiler feed-water pumps

- Condensate pumps

- 2 x HRSG stacks

- 2 x hot-stacks (by-pass stacks) with diverters

- 1 (one) ACC air-cooled condenser and steam ejector vacuum system

Buildings

A multi-story steel-framed building, still unclad, is also available for dismantling and relocation. It currently houses the steam turbine generator and can accommodate offices, the control room and laboratory.

Current Site Conditions

The current site is at 230 m elevation and the local climate is classified as humid sub-tropical.

Average maximum summer temperature is around 31 °C with winter being 14.5 °C.

Air quality at the present site is considered poor with CAQI Index at 80 or above, PM10 particulates above 100 but with no desert dust. The gas turbine combustion air filtration system appears to be adequate

Land Area

The complete plant with evaporation ponds, water treatment facility, fire abatement water storage, extensive switch-yard and sufficient land area set aside for a Phase II expansion capacity of 100 MW expansion, occupies a total land surface area of approximately 420,000 m2 (42 Ha) as evidenced by the attached plant layout plan.

Equipment Warranty

Warranties on main equipment groups by OEMs are available subject to negotiation.

Installed or Partially Installed Equipment (not exhaustive)

Gas Turbine Generators

No. of Gas Turbines				2 trains

Gas turbine model no.				6111 FA+e (extended inspection interval)

Control system 				advanced MK VI

Combustion system				DLN with bleed heating

Inlet Guide Vanes				yes

Place of manufacture				GE Belfort, France

Gas turbine LHV ISO Heat rate		10,140 kJ/kWh

Gas turbine LHV Site Heat rate		Dependent on elevation, output, air temp.

Exhaust gas temperature at ISO		600 C

Fuel						Natural Gas

Fuel feed pressure

Air Flow rate					208 kgs/sec

Feed gas pressure				30 barg (maximum)

Generator Make				BRUSH

Cooling					Air/water

Capacity					95 MVA

Lubricating and Hydraulic system

- A.C. motor-driven dual lube oil pumps

- A.C. motor-driven dual hydraulic pumps used for jacking oil

- D.C. motor-driven, emergency lube oil pump

- AC/DC motor-driven auxiliary, generator oil-seal pump

Filters and Coolers

- Dual lube oil system filters

- Dual hydraulic oil filters

- Dual lube oil coolers

- Plate/frame type with stainless steel plates

- ASME code stamp

- Lube oil coolers

- Lube oil filters

Lube-Oil Piping

- 304L stainless steel lube oil feed pipe Carbon steel lube oil drain pipe

- Lube system valve stainless steel trim

- Lube system valve, stainless steel trim

Lube Oil Mist Eliminator

- Lube vent demister

HRSGs

Number					2 off, 2-pressure with integrated de-aerator

Make						Thermax

Piping and instrumentation			complete

Boiler Feed water Pumps			3 off at capacity 138 m3/hr., 1,325 mwc

Feed pump power requirement		685 kW

HP Steam production per HRSG		113.2 MT/hr.

HP Pressure					98.8 kg/cm2

HP steam temperature				540 °C

LP steam production per HRSG		14.2 m3/ hr.

LP steam pressure				9 kh/cm2

IP steam Temperature				275 °C

Water Purification and Demineralizing

n. 2 off Reverse Osmosis water purification lines.

n. 1 off Demin plant.

Power requirement				pending

STEAM TURBINE

Manufacturer					GE

Type/model					SC2-23. 2-pressure, non-reheat

Inlet pressure	(ambient °C)			95.9 barA (15), 95 barA (30)

Steam Flowrate kgs/s (ambient °C)		8.4 kg/s (15), 7.60 kg/s (30)

Steam Turbine Generator			BRUSH

Volts						11.5 KV

PF						0.8 lag, 0.95 lead

Cooling					Tewac, maximum cooling water temp. 40 °C

Exciter						Brushless

Air-Cooled Condenser

Additional date still outstanding

16 fans

Fan redundancy				not yet known

Fan power consumption			not yet known

Vacuum system				Steam ejectors

Steam Ejector type

Manufacturer

Steam conditions, flow, vacuum

Ejector steam condensation

Photographs

Various site photographs follow below.

Fig.1 GT1 and GT2 and HRSG trains

Fig.2 HRSG elevation with main stack and diverter stack

Fig.3 	 F6FA Gas turbine exhausting to HRSG on the right hand side.

Red container is the CO2 container

Generator circuit breaker (GCB), left edge of the photo and bus-ducting to UAT

Lube-oil skid, bottom right-hand of the picture

(UAT – Unit Auxiliary Transformer)

Fig.4 	 Steam Turbine Hall with ACCC

Fig.5 	 Steam turbine generator in the steam turbine building.

Fig.6 	 Water Treatment and Demin Plant

Fig.7 	 Water Treatment Plant Building and water storage tanks

Fig.8 	 Turbine lube coolers

Fig.9   Step-up transformers

Fig.10 	 Auxiliary Transformers

Fig.11 	 Power plant switchyard and grid connection

E&OE

Annexure

Information Pending

Item #

16.2		STG specification chart

16.3		STG Brochure

16.4		SC2-23 technical information

17		STG BRUSH Generator specifications

18		ACC vacuum steam ejector data sheet, steam conditions

18.2		ACC fans data sheet. Variable speed or fixed?  Redundancy?

18.3		ACC fans operational ambient temperature range

18.4		ACC vacuum system description, steam usage, steam condensation

19		Condenser tank data. Condensate temperature

20		Condensate pumps; number, make, capacity power, data sheet

21		Water treatment plant description and specification, design parameters

Maximum feed-water salinity/contamination

Demineralization plant specifications, chemical usage

22.1		Gas Turbine generator BRUSH generator specifications

22.4		Fuel gas conditioning skid specifications

22.6		Gas feed-in pressure to gas turbine

23		HRSG, as-supplied by Thermax, technical description

23.1		HRSG design point and off-design point performance and operation

23.2		HRSG design code and expected serviceable life of HRSG (ref. Thermax)

50.

51.		Power Plant General Construction standards

100.

100.1		Estimated total parasitic load

Annexure

Major OEM Company Information

(Pending)

GE			General Electric, gas turbines, steam turbines

https://www.ge.com/about-us/history#

ABB			Asea Brown Boveri, Switchgear

https://en.wikipedia.org/wiki/ABB

BRUSH		Generators, electric motors, alternators

https://www.brush.eu/markets/company-history

THERMAX	Thermax Limited

https://www.business-standard.com/company/thermax-4767/information/company-history

GEA			GEA Energietechnik, Germany/ BGR Group India/Enexio

Cooled condensers

ATLAS COPCO