## Sheet1
OEM | Vendor Package | Item | Description | Technical Data | Dimensions / Weight | Quantity
Howden | Howden | SO2 Blower | SAR Blower | SF11.2 Centrifugal Turbo Compressor, Inlet Pressure 0.91 bara Continuous pressure 57 DegC Short time Temperature 65 DegC Electrically driven, required power 1989 kW Speed 4733 rpm Year of Construction: 2021 | Skid (Blower & gearbox): 5m x 5m footprint | 1
Siemens | Howden | Electric Motor | Motor for SO2 blower | Power 2200 kW Voltage 11000 V Frequency 50 Hz Current 132 A Speed 1491 rpm Torque 14091 Nm | 1770mm x 1270mm footprint Weight 8500 kg | 2
Siemens | Siemens | Steam Turbine | Turbine for condensing steam turbine / generator package | SST-300 Industrial Steam Turbine Rated / Max Output 20.29 MW Speed 5314 rpm Inlet steam 37 barg, 376 DegC, 72.5 t/h Admission steam 18.9 Barg, 348.8 DegC, 65.6 t/h Steam Extraction 3.5 barg, 155 DegC, 53.64 t/h Exhaust steam 0.093 bara, 44 DegC | Skid (Turbine & gearbox): 7610mm x 6300mm Skid Weight: 65500 Kg C/W generator & condenser: 23350mm x 10335mm | 1
TDPS | Siemens | Generator | Generator for steam turbine | 20.55 MW 11kV 50 Hz 0.85 pf 1500rpm | 6192mm L x 2765mm W x 3705mm H Weight (in steel container) 42750 Kg | 1
| Siemens | Condenser | Condenser for steam turbine | Shell & tube exchanger, double pass EN 13445 PED Cat III, Module G. Shell min/max pressure -1/1 bar g Steam (shell) design temp 145 DegC Shell MoC P265GH Carbon steel Shell thickness 10-16mm Tubes min/max pressure -1/6 bar g Water (tubes) design temp 85 DegC Tubes MoC 1.4301 Stainless Steel | Shell capacity 51400L Tubes capacity 7700L Weight (empty) 29000 Kg Weight (operating) 39300 Kg 2650mm D x 9650mm L (Height 4890mm with hotwell) | 1
Sigma | Siemens | Condensate extraction pump | Condenser condensate extraction pump | Vertical Condensate pump Sigma 125-CJDV-267-18/2-DU-002-FE EN ISO 5199 MAWT 59 DegC MAWP Suction / Discharge: 0.1 MPa / 0.6 Mpa Speed: 1481 rpm Capacity 110m3/h Delivery head 45m Power 16.9 kW NPSHR 2m | Shaft length (submerged) 2500mm Shaft diameter 120mm Overall length (including motor) 4627mm | 2
Invactech | Siemens | Vacuum Pump | Vacuum pumps (part of vacuum skid for turbine condenser) | Water ring vacuum pump Technical specs unknown |  | 2
Clayton | Clayton | Steam Generators | Steam generators | Clayton Steam Generator Model E-1204-SH Max net heat output 11772kW Modulation range (20-100%) Min/Max output @ 40 barg/380 DegC: 2975/14875 kg/h PSV setting 48barg Min / Max temperature: 4/425 DegC Required gas inlet pressure 400-500mbarg MoC Top, Middle, waterwall superheater: EN10216-2 P235GH MoC Superheater, Bottom: EN-10216-2 16 Mo3 MoC Separator SA-106Gr B | 4823mm x 2784mm x 8931mm Weight (empty) 32000kg Capacity 6800L | 4
Deprest | Clayton | Deaerator Tank | Deaerator for steam generators | ASME VIII Div 1, PED2014/68/EU Cat IV Module G Design Pressure (min/max): FV / 5 barg Design Temperature (min/max): -10/425 DegC MoC shell SA-516 Gr.60 Shell thickness (nominal) 20mm | 9258mm L x 3850mm H, 2500mm Dia (approx) Capacity 42349L Weight (empty) 14000kg Weight (full) 56349kg | 1
Deprest | Clayton | Blowdown Tank | Blowdown tank for steam generators | ASME VIII Div 1, PED2014/68/EU Cat IV Module G Design Pressure (min/max): FV / 10 barg Design Temperature (min/max): -10/184 DegC MoC shell SA-516 Gr.60 Shell thickness (nominal) 12mm | 1600mm dia (approx) x 5100mm H Capacity 8451 L Weight (empty) 3567 kg Weight (full) 12018 kg
Hammelmann | Clayton | Boiler Feedwater pump | BFW pump for Clayton steam generator package | Hammelmann High Pressure Pump (PD) Hampro 202 Max flow rate 61.5l/min - 312 l/min Operating pressure 76 bar g Medium: hot water max temp 140 DegC Crankshaft speed 73-1336 rpm Motor power 75kW Motor speed 105-1500 rpm | Skid 2234mm L x 1324mm W x 1800mm H | 5
Flowserve | Clayton | Boiler Feedwater Booster pump | BFW booster pumps for Clayton steam generator package | Flowserve SIHI ZHND 080200 Medium, water 160 DegC, vapour P 6.18 barg Flow min/max, 29.3/175.2 m3/h Differenntial head 50.2m NPSH R 2.65m Power requirement, 18.54 kW | Skid (including motor) 1324mm L x 540mm footprint | 2
ABB | SPX | Motor | Motor for cooling tower fan | ABB 3GBP282230-ADL + VC 3-Phase squirrel cage motor Power 90 kW 50Hz IP55 | 1200mm L x 80mm W x 100mm H | 6
Various | All | Miscellaneous | Package Ancilliaries | piping, valves, electrical panels etc (lots of it)