- Scope of Supply and Services

List of Contents

Page

  - Steam Turbine – radial exhaust- Alternative 1	2

  - Steam Turbine – axial exhaust- base offer	3

  - Gear Unit	4

  - Lube Oil Plant	5

  - Control Oil Unit	6

  - Surface Condensing Plant	7

  - Miscellaneous	8

  - Spare Parts	10

  - Supervison of Erection, commissioning and trial run (separate

contract)	11

  - Performance test acc. ASME PTC 6.1	12

  - Exclusions from our Scope of Supply and Services	13

  - Limits of Supply	14

  - Standards, Regulations and Guidelines	16

  - Technical Requirements	19

  - Genral Comments on Technical Inquiry Specifications	22

  - List of Major Suppliers for Equipment for Turbogroups	22

i

General remark:

The  quotaed  Scope  includes  all  components  necessary  according  to  Siemens standards for safe and reliable operation of the Turbine.

# Steam Turbine – radial exhaust- Alternative 1

1 Condensing turbine type SST 400 comprising:

- 1 Emergency stop valve, hydraulic, for the live steam inlet, with built-in steam strainer

- 3 Control valves with servo operator for the live steam inlet

- 5 Bleeds

- Reverse flow protections for bleeds as shown in P&ID (loose supply)

## Radial exhaust

- Control system for speed, power (see chapter 6)

- Turbine protection (see chapter 6)

- Mat-type insulation

- Internal steam pipes with valves for balance piston, sealing steam and leak steam

- Internal pipes for drain system with valves

- Internal oil pipes for the lube and control oil system with valves

- Start-up drains with pneumatic operated shut-off valves

- Operating drains

- Baseframe for the turbine

- Earth terminal

- Boroscope openings in the turbine casing

- Sealing steam pressure control (sealing steam from live steam)

- 1 Connection for air dryer (dehumidifier)

- 1 Sealing steam cooler for the rear labyrinths

- Standard preservation (6 months) as per Siemens - factory standard

- Prime coat and finishing coat of paint as per Siemens - factory standard

- Touch up paint to Site

- Operation manual, 3-fold, English langauge

# Steam Turbine – axial exhaust- base offer

1 Condensing turbine type SST 400 comprising:

- 1 Emergency stop valve, hydraulic, for the live steam inlet, with built-in steam strainer

- 3 Control valves with servo operator for the live steam inlet

- 5 Bleeds

- Reverse flow protections for bleeds as shown in P&ID (loose supply)

## Axial exhaust

- Control system for speed, power (see chapter 6)

- Turbine protection (see chapter 6)

- Mat-type insulation

- Internal steam pipes with valves for balance piston, sealing steam and leak steam

- Internal pipes for drain system with valves

- Internal oil pipes for the lube and control oil system with valves

- Start-up drains with pneumatic operated shut-off valves

- Operating drains

- Flash box (optional)

- Baseframe for the turbine

- Earth terminal

- Boroscope openings in the turbine casing

- Sealing steam pressure control (sealing steam from live steam)

- 1 Connection for air dryer (dehumidifier)

- 1 Sealing steam cooler for the rear labyrinths

- Standard preservation (6 months) as per Siemens - factory standard

- Prime coat and finishing coat of paint as per Siemens - factory standard

- Touch up paint to Site

- Operation manual, 3-fold, in English

i

Gear Unit

Single helical high-speed parallel-shaft gear with:

- Flanges for coupling guard on pinion and gear shaft

- Hollow shaft between turbine and gear unit

- Coupling guard between turbine and gear unit

- Coupling (quillshaft) between gear unit and generator

- Coupling cover between gear unit and generator

- Built-on barring gear with electric motor, coupling and softstarter

- Built-on main oil pump

- 6 Resistance thermometers wired to terminal box

( 1 x for each radial bearing, 1 x for each side of thrust bearing)

- Shaft vibration pick-up wired to terminal box

- Base frame for the gear unit, as oil tank

- on the base frame are arranged: 1 electrical operated full load standby oil pump, 1 electrical operated emergency oil pump, 1 double oil cooler (2 x 100%), 1 double oil filter (2 x 100%), 1 oil vapour extractor, 1 jacking oil pump

- Foundation anchors, -bolts and leveling spindles

- Inspection documents acc. to EN 10204

- Trial run acc. to the Siemens standard test program

- Painting acc. to factory standard

- Preservation acc. to factory standard

# Lube Oil Plant

Design of the oil plant according to the manufacturer's standard Design of the oil coolers according to DIN

The lube oil plant arranged on the gear package with integrated oil tank comprises following main parts:

- 100% auxiliary oil pump, three-phase a.c. motor driven

- approx. 40 % emergency oil pump, d.c. motor driven

- Jacking oil pump, three-phase a.c. motor driven

- Oil vapor extractor with three-phase a.c. motor

- Oil tank heater (electric immersion heater for Tamb. < 15°C)

- 2  x  100  %  oil  coolers  (tubes  made  of  CuZn28Sn  and  tube  sheets  made  of CuZn38SnAlF39)

- 2 x 100 % lube oil filters

- Change-over  device  (oil  cooler  and  oil  filter)  for  switching  operations  without interruption of the oil supply

- Pressure control for the lube oil

- Oil safety valve

### additional accesoires:

- Direct driven main oil pump (at the gear unit)

# Control Oil Unit

The hydraulic supply unit is installed on a separate skid ready for operation and consists of the following main parts:

- 2 x 100% displacement piston type pumps, AC motor driven

- 1 oil tank

- 1 oil accumulator

- 2 x 100% oil filter with change over device

- 1 off-line cooling pump, AC motor driven

- 1 oil cooler (oil/air) with fan

- Interconnecting oil pipes (stainless steel) with valves

# Surface Condensing Plant

Not in Siemens’ scope of supply

Optional : Siemens will submit the following documents of the main condenser Incl. in Siemens scope for engineering support is:

    - the thermodynamic design data

based on customer material specification provided in advanced

    - assembly drawing

    - mechanical data sheet including the following.:

    - dimensions of tubes

    - tube sheet

    - shell

    - allocation of tube bundles in tube sheet. Excluded from Siemens scope  is the following :

    - any kind of liability and guarantee

    - support during manufacturing and installation

    - detailed manufacture drawings

    - quality control of manufacture

The design / supply of the ejector unit including condensate pumps, ejectors, inter and after condenser and control valves and interconnecting piping are not in Siemens scope.

# Miscellaneous

## ALTERNATIVE 1:

- Spring elements for the turbine table

- Basic & detail engineering

- Documentation in ENGLISH

- Packing for transportation

- Freight FOB, north German seaport, in accordance with INCOTERMS 2000

- Turbine anchor bolts if required by Siemens

## Base offer :

- Basic & detail engineering

- Documentation in ENGLISH

- Packing for transportation

- Freight FOB, north German seaport, in accordance with INCOTERMS 2000

- Turbine anchor bolts if required by Siemens

- List of special tools required for erection

## Steam turbine

  - Blow out device for trip valve

  - Aligning device (shaft)

  - Container for the special tools

# Spare Parts

One set for two years of continuous operation we recommend the following spare parts:

### Steam turbine

- 1 Set of pads for the main bearings of the turbine (radial and axial bearings)

- 1 Set of oil sealing rings for these bearings

- 1 Set of sealing strips with caulking wires for the shaft labyrinths

- 1 Set packings and spindles for control valves

### Gear unit

- 1 Set of bearings for the pinion and the wheel shaft

- 1 Set of shaft sealing rings

### Oil units

- 1 Set gaskets

- 1 pc. Pressure regulation valve cone

- 1 Set lubrication oil filter elements

- 1 Set control oil filter elements

### Instrumentation

- 1 pc. Pick-up for speed

- 1 pc. Pick-up for axial displacement

- 2 pc. Pick-up for shaft vibration

- 2 pc. RTD for bearing temperature – turbine

- 2 pc. RTD for bearing temperature – gear unit

- 1 pc. Pressure switch (valve block)

- 1 pc. Position transducer (steam control valve)

- 2 pc. Instrument 3-way valve

- 1 pc. O-Ring

### Generator

Not included in the offer

# Supervison of Erection, commissioning and trial run (separate contract)

The scope of service, based on daily rates, includes the following: The assignment of personnel (and, if applicable, the tools) for:

- the supervision of the erection (ready for commissioning)

- the preparation of commissioning

- the commissioning

- Training on the job during commissioning

- Classroom training (Option), see separate proposal in Ch. 8

- the trial run (3 days, 10 hours daily with recall standby)

- Performance test acc. to ASME PTC 6.1 under conditions specified in section 8.3

An erection / commissioning coordination meeting shall be held before erection & commissioning activities.

See also chapter 8 “Erection time schedule” and "Specification of technical field assistance".

# Performance test acc. ASME PTC 6.1

The turbine unit will be tested in accordance with ASME PTC 6.1 as dicreibed in section 8.03 “conditions for Performance test. The test shall be carried out within three months after the provisional acceptance of the turbine, but no later than six months after first steam to turbine. During the performance test the plant will be operated under the responsibility of the customer taking due account of the operating instructions. The reports on beginning, course and end of the performance tests as issued by the supplier must be signed by the customer.

Performance test will be carried out by third party (not in Siemens scope)

### Siemens scope of supply:

Test supervisor Precision instruments

Fitting and removal of Siemens’s precision instruments

### Performances by others:

Labour, normal operating personnel, helpers etc. Nozzles for flow measurements

Calibrated measuring transformers (3-phase) for power measurement Necessary pressure taps outside Siemens delivery limits

Necessary temperature pockets outside Siemens delivery limits

### Duration:

Three up to five days for the installation of Siemens-measuring instruments. Two days each loadpoint for the calibration and testing.

If the test should be delayed due to reasons beyond Siemens control, any additional cost for Siemens personnel and instruments will be charged.

### Number of test points:

The performance test will be carried out for one load point.

### Tolerances:

The tolerances which are mentioned in the test instructions will be applied.

i

Exclusions from our Scope of Supply and Services

### Steam Turboset

The following components and services are not included in our scope of supply:

- Live steam pipe up to the live-steam emergency-stop valve

- Condenser and Condensing system components

- Spacer / Interconnecting piece Turbine – main condenser

- Condensate sampeling / analysing system

- Tube cleaning system of main condenser

- Bleed steam pipes from turbine nozzle to the bleed non-return flap valve and from there to the bleed steam system

- Cooling water pipes with isolating valves to and from the connecting nozzles

of the corresponding equipment

- Safety valves in the steam, bleed, and water pipes

- Electric cables, switches, contactors and fuses

- Foundations, earthworks, soil preparation

- Spring elements (not required in case of base offer)

- Dehumidifier

- Grouting of baseframe with non shrinking material

- Masonry

- Heating and lighting of the machine house

- Compressed air, water and power supply on site

- Shop test run

- Manufacturing drawings

- Guarantee measurements

- Machine house crane

- Steel structures, platforms, pedestals

- Auxiliary systems, such as cooling water circuit etc.

- HP and LP bypass stations

- Lightning protection and earthing system

- Fire fighting equipment

- First oil filling

- Calculation of the foundation

- Noise hood or Hood for outdoor installation

- Generator and accessories (only one generator is included for Turbine 1)

- Pressure reducing or by pass station

- Interconnecting oil piping between oil system and Generator

- Vent steam condenser

General remark:

All systems connected to the turbine have to be self-protected in acc. with DGRL 9723EG

# Limits of Supply

### Steam

Inlet connection of the turbine live-steam emergency-trip valve Outlet flanges of the turbine bleeds

Inlet and outlet flanges of the bleed non-return flap valves Outlet connection on turbine exhaust

Inlet flanges of the sealing steam pressure control valves

### Cooling Water

Inlet and outlet flanges of the oil coolers

Inlet and outlet flanges of the generator (only in case generator is in Siemens scope of supply)

### Drains

Outlet flange of the falsh box

### Electric Current

Connecting terminals of the electric motors Connecting terminals of the solenoid valves

Connecting terminals for terminal strip (group terminal) Connecting terminals inside the cubicles

### Oil

Filling connection on turbine oil tank

Inlet / Outlet flange on oil reservoir to the generator (both lubricating oil & lifting oil)

### Air (Compressed Air and Instrument Air)

Connection at the control equipment

General remark:

In general the piping interface to customer shall be according to Siemens standard i.e. welding or Flanges. In case of Flanges it shall be according to ANSI. Counter flanges, bolts and interconnecting piececs will be supplied by Kaidi.

Siemens will submit during detailed engineering a detailed list, including detailed flange, bolts, nuts,gaskets…etc informations, of all customer’s connections.

For further details please refer to attached P&I Diagrams in Chaper 7

Limits of Supply

To define the limits of supply the following symbol is used in the P&I diagrams: (see chapter 7)

S C

Customer/Others Siemens

# Standards, Regulations and Guidelines

The applicable standards, regulations and guidelines valid at the time of tender submission form the basis for planning and supply of the equipment, except for deviations that are specified in the list of deviations and clarifications.

Unless otherwise agreed, we use the power system designation system KKS, last edition. In respect of numbering, a more detailed system incorporating suitable producer-related groups of numbers is employed in addition.

### Basic Standards

Unless other basic standards have been agreed upon with the customer, the quotation of SIEMENS is based on European standards and international standards (EN, DIN, IEC etc.) and the following standards, as far as the equipment covered therein is part of the scope of supply:

### Main Components

- Turbine with pressure casing and pressure oil system acc. to DIN 4312.

- Gear units acc. to AGMA 421.06

- Generator acc. to European IEC-Standards

- Condenser: mechanical strength acc. to AD-regulations, bases on VGB-R455P, thermal rating acc. to HEI.

### Pipes and Connections

- Internal design of steam and condensate pipes acc. to DIN 2413.

- Oil pipes made of stainless steel, seam welded

- Flanged connections in the oil system PN16 acc. to DIN EN 1092-1, contact surface acc. to Form B.

- Flanged connections in the steam area acc. to DIN EN 1092-1

### Plant Control and Instrumentation

- Vibration severity acc. to ISO 10816, shaft vibrations acc. to ISO 7919.

Probes acc. to DIN 43 760.

### Protection

- Earthing acc. to VDE 0100 and 0141, identification acc. to DIN 40 011.

### Inspection and Testing

- Examinations and tests according to the E&T Plan of SIEMENS. Certificates acc. to EN 10 204-2.2 and 3.1.

- The thermal acceptance tests of steam turbines are performed acc. to DIN 1943. (VDI-Steam Turbine Code)

- Examination and acceptance of pipes and connections acc. to DIN EN 1127.

- Non destructive tests acc. to DIN EN 1559

- Qualification testing of welders acc. to DIN-EN 287.

### Welding

- Welding procedure acc. to DIN EN 15614.

### Noise

- Sound measurement acc. to EN ISO 4871.

### Insulation

- The insulation thickness is determined in accordance with our factory standard based on DIN 18 421 and VDI 2065. Material certificate acc. to VDI 2055.

### Painting / Preservation

- De-rusting in accordance with the Swedish standard SA 2,5, similar as DIN 55928.

- Prime coat of paint acc. to manufacturer‘s standard.

- Final painting acc. to manufacturer‘s standard.

- Preservation	for	non-painted	surfaces	acc.	to	manufacturer‘s	standard	in accordance with VGB-R 116 H.

### Electrical Systems

- Electric motors: Rating classes acc. to IEC 34. Standard motors acc. to IEC 72 and DIN 42 677.

- Cables for voltages up to 60 V acc. to VDE 0815.

### Miscellaneous

- Turbine oil acc. to ISO, viscosity VG 46.

- Material strength design of the heat exchangers acc. to AD-Code of Practice, DIN materials acc. to VGB-R455P table 3.

- Deviations and tolerances for tube bundles and heat exchangers acc. to DIN 28 008.

- Design of steam ejectors and vacuum pumps acc. to VGB-R 126 L.

- Bolts acc. to DIN 933, nuts acc. to DIN 934. Bolted joints on pressure casings acc. to DIN 938/939. Admissible stresses in the bolts acc. to DIN ISO 898 / DIN 17240, in the nuts acc. to DIN 267.

- Denominations acc. to DIN 19 227 in accordance with SI basic units acc. to DIN 1301.

- Symbols on P&I D`s acc. to ISO 10628.

- Blowing  out  of  steam  piping  in  accordance  with  Siemens  factory  standard 1CWN002896.

# Technical Requirements

### Oil Specification

For the common lube and control oil system for turbine, gearing (if applicable) and driven unit, mineral oil must be used  in  accordance  with  DIN  Standard  51515 (May 1978) and have the following properties:.

Designation                                Requirement                               Test Method

Lube oil type                                  TD 46

ISO viscosity class                         ISO VG 46                                   DIN 51519

Hitherto           existing           code 	25

number (correlation)

Kinematic viscosity at 40°C           min. 41.4      mm2/ s (cSt)           DIN 51550

max. 50.6	mm2/ s (cSt)	in connection with

DIN 51561 or

DIN 51562

Mean dynamic viscosity at 40°C	41.4 x 10-3	Pa s

Viscosity index not less than	95

Density at 15°C not more than	0.90	kg/l	DIN 51757 Flash point (Cleveland)

not less than	185	°C	DIN 51376

Pourpoint equal to or less than	-6	°C	DIN 51597

Neutralisation number	DIN 51558

not more than	0.1 *)	mgKOH/g	Part 1 Max. saponification number	0.15 *)	mgKOG/g	DIN 51559

Max. ash content (oxide ash)

not more than	0.01 *)	% by weight

Water content	g/100g	below the limit of quantifiable

detectability	DIN 51582

| Content of foreign solids | below the limit of quantifiable |  |
| --- | --- | --- |
| g/100g | detectability | DIN 51592 |

| Designation Demulsification number | Requirement max. 300 | sec. | Test Method DIN 51589 |
| --- | --- | --- | --- |
|  |  |  | Part 1 |
| De-airability (air release property) at 50°C | max. 5 | min | DIN 51581 |
| Corrosion influence on copper, |  |  | DIN 51759 |
| corrosion degree | max. 2-100 A3 |  | (3h at 100°C) |
| Corrosion protection property against steel | 0 - A (free of corrosion) |  | DIN 51585 |
| Ageing behaviour Increase of neutralisation number after 1000 h | max.2.0 mg KOH / g oil |  | DIN 51587 |
| Spec. loadability (gear unit) | 6 - 7 Damage power stage **) FZG Normal test IP 166/65 |  | DIN 51354 (A/8, 3/90) ASTM D 1976 |

*)	As additives are used, these values are higher and are to be stated by the supplier.

Oils with additive materials contain deterioration and corrosion protection as well as additive which prevent foaming.

NOTE:

EP additives increase the specific loadability (mechanical limiting load)

- with EP additives (FZG >7):	turbosets with gear units

- without EP additives(FZG <7):	turbosets without gear units

Refer to the lube oil specification of the gear manufacturer in this regard.

**)	Not included in DIN 51515.

### Steam purity requirements

Guidelines for the inlet steam condensate

Kindly refer to the attachment, 02_Appendix_2.3_Steam_Purity_Requirement.pdf, for the recommended steam quality.

Monitoring

We strongly recommend the continous monitoring of the water/steam cycle by constantly recording the electric conductivity (at 25 °C) at a local sampling point downstream of the strongly acidic cation exchanger, and the determination of the silicia content. The monitoring equipment should be installed on the inlet steam and condensate sides.

# Genral Comments on Technical Inquiry Specifications

Our supplies and services shall be designed in accordance with those standards, guidelines and specifications applicable within Germany and Europe. The customer’s piping interface will be ANSI flange connections . In addition, Siemens has developed internal guidelines and specifications for implementation, based on its many years of experience	with          steam          turbine           generation           plants. This ensures a high degree of safety and availability.

# List of Major Suppliers for Equipment for Turbogroups

Siemens cooperates with approved suppliers and procures equipment and materials world wide at competitive price levels. It is not possible therefore to name single subcontractors for the various items of the power plant.

The subsuppliers are approved by Siemens. Siemens may also consider other equivalent approved suppliers and reserves the right to select an equivalent supplier.

Kindly refer to 02_Appendix_2.2_Siemens_Subsuppliers_List.pdf for the list of sub- suppliers.