Brand New

30 MW Siemens Turbine Generator

TYPE:	SST 400

condensing  steam  turbine  with  four  bleeds and one extraction

| TURBOSE OUTPUT: (at generator terminals) - Normal | 30 | MW |
| --- | --- | --- |
| - Maximal | 31,88 | MW |
| - Minimal | 4,5 | MW |
| SPEEDS: - rated – turbine | 5038 | rpm |
| - rated – generator | 1500 | rpm |
| - emergency trip (turbine) 110% - resonance (turbine) 1. natural frequency | 5542 2620 | rpm rpm |
| 2. natural frequency | 6398 | rpm |
| - torsional critical (complete train) | 18,0 | Hz |
|  | 61,3 | Hz |
|  | 152,7 | Hz |

DIRECTION OF ROTATION	c.w. (seen in the direction of steam flow)

LIVE STEAM:

- pressure  rated	127	bar(g)

max.	133,4	bar(g)

- temperature rated	535	°C

max.	543	°C

- temperature change

temperature jump, max. permiss.	±20	°C

subsequent rate of temp. change	±2	°C/min

rate  of  temp.  change,  max.  permiss  (without previous temp. jump)

±5	°C/min

- steam flow  max.	128,6	t/h

- short time deviations acc. to IEC 45-1		see also Section 6 pressure increase  max 12 h/a	152,6	bar(g)

temperature increase  max. 400 h/a	549	°C

- steam quality	see Section 6

4TH  BLEED

- pressure	33,377	bar(g)

- steam flow	7,67	t/h

3RD  BLEED

- pressure	17,856	bar(g)

- steam flow	5,71	t/h

Turbine Specifications

| EXTRACTION |  |  |
| --- | --- | --- |
| - pressure | 9,0 | bar(g) |
| - steam flow | 7,60 | t/h |

| 2ND BLEED - pressure | 2,811 | bar(g) |
| --- | --- | --- |
| - steam flow | 8,16 | t/h |
| 1ST BLEED - pressure | -0,104/0,896 | bar(g)/bar(a) |
| - steam flow | 8,64 | t/h |
| EXHAUST: - pressure rated | -0,932/0,068 | bar(g)/bar(a) |
| - steam temperature | 38 | °C |
| - steam flow | 82 | t/h |

| LOAD POINTS | No extraction | 70 t/h extraction |  |
| --- | --- | --- | --- |
| Guarantee Loadpoint Output at the generator terminals | T 31230 | 17990 | kW |
| Turbine operating speed | 5 000 | 5 000 | rpm |
| Power factor cosφ | 0,85 | 0,85 |  |
| Live steam: inlet pressure | 128 | 128 | bar(a) |
| inlet temperature | 535 | 535 | °C |
| inlet flow 1st bleed pressure | 119,77 0,896 | 119,77 0,115 | t/h bar(a) |
| flow 2nd bleed pressure | 8,64 3,811 | 2,31 0,525 | t/h bar(a) |
| flow Extraction pressure | 8,16 10 | 4,71 10 | t/h bar(a) |
| flow 3rd bleed pressure | 7,60 18,856 | 87,3 18,848 | t/h bar(a) |
| flow 4th bleed pressure | 5,71 34,377 | 5,71 34,345 | t/h bar(a) |
| flow Outlet pressure | 7,67 0,068 | 7,66 0,041 | t/h bar(a) |
| flow | 81,65 | 11,70 | t/h |

Page 2 / 2