120 ton/Hr Coal Fired CFB Boiler, 30 MW Steam Power Plant Price Offer

PROPOSAL:

120 T/H Coal Fired CFB Boiler + 30 MW Steam Turbine Power Plant

We, THE VENDOR  take pleasure in submitting your esteemed company an offer for the planned 120 T/H CFB Boiler + 30 MW Power Plant, which will be built in USA as the captive

power plant.

This proposal covers all technical processing systems necessary and suitable for the Power Plant, including supply of equipments (BTG), auxiliaries and material which shall form a complete power plant after being installed, as well as service provided , such as supervision of installation & erection and commissioning/test-running, etc.

### System in the Power Plant:

- Electric system: High voltage (11 kV) electricity from generator outgoing feeder panel; Low voltage (440V) system for supply electricity to power plant itself only.

- Combustion and Thermal System

- Boiler + Condensing Steam turbine/Generator, Condenser, Unit Auxiliaries for boiler, steam turbine and generator.

- Fuel Supply System Coal feeder, Belt conveyer, etc.

- Ash/Slag Handling System Dust Collector, IDF, chimney, slag conveyer, etc.

- Boiler Water Treatment System, RO device

- PLC + IC: Boilers, turbines and generators to be centralized in Master Control Room, while water treatment, coal conveyor, etc. to be controlled at spot.

### Scope of Work:

- Design & drawings for system technology, equipment foundation, installation, etc.

- Supply of machinery, equipment, device, instrument, auxiliaries, material, etc.

- Supervision Installation/erection for the equipment/systems in the power plant.

- Commissioning, Trial run and operation.

- Training for owner's staff during installation and commissioning, and extra 1-month training.

### 120 TPH CFB Boiler Specification and Technical Data:

- Brand: Babcock & Wilcox

- Circulating Fluidized Bed Boiler

- Boiler capacity: 120 Ton/Hr

- Steam Pressure: 130 bar

- Steam Temperature: 535oC

- Fuel: Coal

- CO controlled through combustion management.

- SO2 controlled through an injection of pulverized limestone into boiler.

### 30 MW Steam Turbines Specification and Technical Data

TYPE:	SST 400

condensing steam turbine with four bleeds and one extraction

| TURBOSE OUTPUT: (at generator terminals) - Normal | 30 | MW |
| --- | --- | --- |
| - Maximal | 31,88 | MW |
| - Minimal | 4,5 | MW |
| SPEEDS: - rated – turbine | 5038 | rpm |
| - rated – generator | 1500 | rpm |
| BROCHURE ATTACHED |  |  |

### Related Information:

- Supervision of Installation/erection and Commissioning/running-test

When the site preparation is complete (civil work is finished and some equipment’s have arrived at site), the installation/erection shall start.

The power plant equipment’s/systems installation will last for 14 months.

The supplier shall be responsible for the installation work. Normally, 40-50 technician & workers are required (100-15 persons at peak time).

Vendor will send 20~25 engineers for site supervision of installation & erection. Power plant commissioning/running-test will last for 1 month

- Training and O&M Service:

Except for the training during installation and commissioning period, vendor would like to provide 1-month extra training and O&M service after hand-over.

Project Time Schedule:

The power plant shall be completed within 18 months. ( 1 more month as adjustment period)

- Installation drawings: after receiving deposit (down payment) 4 months for 1st lot; 4 month for 2nd lot;

- Equipment & materials shipment:

1 lot: 6 months from down payment (boiler & auxiliaries)

- Installation/Erection:

8 months from arrival of shipment

- Commissioning/Running Test:

2 month

### Owner’s Scope of Work:

Apart from the investment for items mentioned above, vendor would like to indicate the information for the Power Plant as reference for Owner:

- Items to be considered and held by Owner Electricity (50Hz, 380V or 400V) Cranes

Fuel/Oil/Lubrication Chemical materials

Instruments & Apparatus for Testing

- About construction by the Owner

Civil work, foundation, structure and buildings for the power plant Roads/Walls/Out-door

lighting for the power plant Water feeding/drainage

Power substation and transmission lines outside the power plant Facilities and auxiliary Facilities in the power plant Ventilation, air-conditioning, communication and fire-fighting Maintenance workshop, logistics department, warehouses in the power plant Supplementary and subsidiary body in the power plant, if any

- Taxation  and  Permit  in USA  Taxation, custom duties, VAT, local tax, etc.

Costs regarding final site preparation and Tests Costs regarding the construction permits and its cost Permits for the power plant and its cost

- Transportation and Freight in USA and overseas.

Costs regarding transportation of machinery equipment, freight of machinery and clearance of machinery are totally in customer’s scope.

- THE VENDOR  shall carry out the work of designing, supply of necessary.	Equipment  &  materials,  providing  supervision

services  for  supervision  of  installation/erection  as  well  as commissioning /running-test.

- Simultaneously, Owner shall be responsible for supplying the other buildings, and providing facilities, supplementary, subsidiary body (if any) as required, so as to complete the project of the Power Plant.

THE VENDOR  has not quote the air tickets & visa costs of the supervision engineers in this offer. The owner should be responsible for THE VENDOR  Engineers' meals, accommodation,

transportation, office, insurance, communication and safety during their stay in USA.

#### Prepared By	Checked By	Approved By

| M Usman Ali | Farhat Abbas | Zahid Latif |
| --- | --- | --- |
| Application Engineer | Director Marketing | CEO |

The vendor  Energy Systems (Private) Ltd.

###### Industrial Steam Turbines

SST-400 Steam Turbine

## Up to 65 MW

SST-400 Steam Turbine

Overview

The SST-400 is a single casing steam turbine, providing geared or direct drive to 50 and 60 Hz generators, or to compressors and pumps. The symmetrical casing with horizontal joint flange enable the SST-400 to accept short start-up times and rapid load changes.

The modular package design allows a wide variety of configurations to satisfy the customer’s individual needs in the most economical way. The utilization of selected proven components assures high reliability and easy maintenance.

Turbine layout

Typical applications of the SST-400 include:

Industrial power plants, e.g. captive power plants in the chemical industry, sugar industry, textile industry, in pulp and paper mills, steel works, mines

Cogeneration and district heating plants Concentrated Solar Power (CSP) plants Geothermal power plants (SST-400 GEO) Biomass plants, waste to energy, e.g. waste

incinerators, waste heat from chemical processes

Combined cycle power plant

Height:

8.5 m (28 ft)

2

SST-400 – design features

The SST-400 is available as a back pressure or condensing turbine with internally controlled extraction and possibil- ity of several bleeds. The blading design provides for high efficiency over the whole operation range, giving the customer highly flexible plant operation. The design of the exhaust blades allows large exhaust areas with high thermodynamic efficiency and reliability. With a separate internal casing, the steam turbine can also be used as a single casing reheat turbine.

Operational flexibility

The turbine has a symmetrical casing with horizontal joint flange, which allows short start-up times and rapid load changes. The design of all supports for labyrinths and blade carriers ensures flexibility for the whole turbine. Internal valve arrangements, controlling the steam flow to the back end of the turbine, are used to maintain constant process steam extraction pressures over a wide flow range.

The rotor of the SST-400 range is made of solid forging and is fitted with resonance-resistant blading. The reduction

gears are taken from the existing range of world class gear manufacturers and have proven high reliability and performance.

Reliability and efficiency from proven technology

The SST-400 single casing turbine can be equipped  with upward, downward or axial exhaust to fit with the selected installation. The turbine skid can be combined with standardized gearbox-oil units and generators to a

turboset, according to the customer’s needs. The turbine skid and gearbox / oil unit are fully assembled in the workshop before being shipped to the site.

Easy maintenance

Our proven installation and maintenance concept lowers maintenance cost by enabling easy access to the installed components, the turbine, gearbox, and generator. Several maintenance concepts are available for different modes of operation.

Design features Customized steam path Proven

Modular Thermoflexible design

Customer benefits

Fast and early layout planning

Short delivery time Compact design minimizes

space requirements of

installation

Easy access to mechanical com- ponents facilitates maintenance

Remote control for simple operation High reliability/availability

High efficiency

Back pressure exhaust

Condensing exhaust

Turbines

Gears Generators

Exhaust area

1,3–3,0 m2 (14.0–32.3 sq.ft)

Modular concept for SST-400 turboset

3

# SST-400 GEO for Geothermal Plants

The SST-400 GEO is a derivative of the SST-400 turbine, optimized for the harsh conditions of geothermal steam cycles. The SST-400 GEO is used in geothermal applica- tions with superheated direct steam, flash or combined cycle, offering an outstanding reliability, flexibility and economy of operation.

High performance butterfly control and trip valves are designed for demanding geothermal steam environment. These components are an integral part of the control, monitoring and safety system that utilize the operator friendly SIMATIC S7 that easily interfaces with plant DCS. These systems have been designed to meet the demand- ing EC and international safety standards and leverage the strength of Siemens and TurboCare.

SST-400 GEO turbine

Proven technology

The SST-400 GEO is a joint development between Siemens and the geothermal steam turbine service provider TurboCare. The turbine combines the proven turbine casing of the Siemens SST-400 as well as the steam turboset accessories (gears, generator, base frame) with the geothermal steam path and moisture removal features of the TurboCare Magma turbine family.

is a world leader in steam turbine technology, offer- ing versatile, reliable and proven industrial steam turbines which meet all customer requirements for economic installation and operation.

through long experience in the after-market, is well known in the industry for turbomachinery services and improving reliability, efficiency and output of Geothermal power plants.

4

SST-400 GEO design features

Robust impulse design and generous clearances result in sustained efficiency and high reliability

Proven steam path for optimized reliability with low steam parameters

Ground floor installation

Package solution for faster installation and commissioning

Advanced highly effective moisture removal techniques

Ease of maintenance due to inlets in casing lower half

Moisture separators of the SST-400 GEO

Blades

Integral shrouds (continuous coupled) to lower alter- nating stress and resist corrosion-assisted fatigue

Laser applied Stellite alloy on last stage

Modern airfoil shapes to improve turbine efficiency Widely spaced nozzles to resist fouling from deposits Modern dovetails that reduce peak stress and resist

stress corrosion cracking

Materials

Special material selection to meet geothermal specific steam chemistry and to resist corrosion attacks and corrosion-assisted fatigue cracking:

12 Cr diaphragms

2% Cr integral forged rotor; 12% Cr optional

X-15 & 17-4 blades standard, Titanium and Inconel optional

Moisture separators pull moisture from the steam at the tip of the blade. The condensate must be removed from the casing at each stage to minimize erosion and improve performance due to the “Reheat Effect”.

When humidity is removed before the steam enters the next turbine stage, the steam proceeding through the turbine shifts to a higher quality

(less moisture), as a result from a higher enthalpy. When the enthalpy of the steam going through  the turbine increases, the steam turbine efficiency improves as well. That is referred to as the “Reheat effect.”

5

# Installation and maintenance

Our proven installation and maintenance concept lowers maintenance cost by enabling easy access to the installed components - the turbine, gearbox, generator and auxilia- ries. Our service solutions are based on long experience of taking care of a substantial global fleet. This experience is incorporated systematically into our design and manufac- turing as well as our service and maintenance practice, making Siemens a reliable partner now and in the future.

We are able to provide comprehensive spare-part service, repairs and maintenance solutions designed to increase the reliability and availability of the plant. Our retrofit so- lutions return turbines to the state of the art even after a normal operating life. Long-term maintenance contracts assure prolonged plant operation at predefined costs.

Remote monitoring

As all SST-400 and SST-400 GEO turbines are prepared for remote monitoring, Siemens offers service contracts for condition-based maintenance, customized for the specific operating status of each machine to reduce outage and overhaul costs. Using the remote monitoring technology, customers are able to get fast telephone advice and secure remote support, online help, advanced trouble- shooting and intervention, provided by specialist person- nel who know the plant’s design and understand its operation.

# Reference examples

SST-400, Burnaby, BC, Canada; 25 MW.

The condensing extraction turbine powers an incineration plant.

SST-400, Haldia, India; 35 MW.

Manufacturing of the condensing turbine at the workshop.

6	66

SST-400, Kayseri, Turkey; 35.5 MW.

Condensing turbine for a combined cycle plant.

The Blundell Geothermal Plant in Milford, Utah (USA), uses a 26 MW TurboCare condensing turbine with SST-400 GEO steam path.

SST-400 technical data

Power output 50 or 60 Hz, up to 65 MW Speed range 3000–8000 rpm

Live steam conditions

Pressure up to 140 bara / 2030 psia Temperature up to 540°C / 1004°F

Hot reheat conditions

Pressure up to 30 bara / 435 psia Temperature up to 450°C / 842°F

Bleed up to 60 bara / 870 psia Controlled extraction (single or double)

Pressure up to 45 bara / 653 psia

Temperature up to 450°C / 842°F

Exhaust steam conditions

Back pressure up to 25 bara / 363 psia District heating up to 3 bara / 43 psia Condensing up to 0.6 bara / 8.7 psia

SST-400 GEO technical data

Power output

50 or 60 Hz, 5–55 MW (condensing)

50 or 60 Hz, 5–60 MW (non-condensing)

Speed range 3000–6000 rpm Live steam conditions

Pressure up to 12 bara / 175 psia Temperature up to 250°C / 482°F

Exhaust steam conditions Condensing up to 0.4 bara / 5.8 psia

Non-condensing up to 1.4 bara / 20 psia

All data are approximate and project-related.

7

Published by and copyright © 2011: Siemens AG

Energy Sector Freyeslebenstrasse 1

91058 Erlangen, Germany

Siemens AG

Energy Sector Oil & Gas Division Wolfgang-Reuter-Platz

47053 Duisburg, Germany

Siemens AG

Lutherstr. 51, 02826 Goerlitz, Germany

Siemens Energy Inc. 10730 Telge Road

Houston, Texas 77095, USA

For more information, please contact our Customer Support Center.  Phone: +49 180 524 70 00

Fax:	+49 180 524 24 71

(Charges depending on provider)

- mail:   support.energy@siemens.com

Order No. E50001-G410-A114-X-4A00

Printed in Germany

Dispo 34806, c4bs 7477 bdk 110159 P WS 10112.2

Printed on elementary chlorine-free bleached paper.

All rights reserved.

Trademarks mentioned in this document are the property of Siemens AG, its affiliates or their respective owners.

Subject to change without prior notice. The information in this document contains general descriptions of the technical options available, which may not apply in all cases.

The required technical options should therefore be specified in the contract.

###### www.siemens.com/energy

- Scope of Supply and Services

List of Contents

Page

  - Steam Turbine – radial exhaust- Alternative 1	2

  - Steam Turbine – axial exhaust- base offer	3

  - Gear Unit	4

  - Lube Oil Plant	5

  - Control Oil Unit	6

  - Surface Condensing Plant	7

  - Miscellaneous	8

  - Spare Parts	10

  - Supervison of Erection, commissioning and trial run (separate

contract)	11

  - Performance test acc. ASME PTC 6.1	12

  - Exclusions from our Scope of Supply and Services	13

  - Limits of Supply	14

  - Standards, Regulations and Guidelines	16

  - Technical Requirements	19

  - Genral Comments on Technical Inquiry Specifications	22

  - List of Major Suppliers for Equipment for Turbogroups	22

i

General remark:

The  quotaed  Scope  includes  all  components  necessary  according  to  Siemens standards for safe and reliable operation of the Turbine.

### Steam Turbine – radial exhaust- Alternative 1

1 Condensing turbine type SST 400 comprising:

  - 1 Emergency stop valve, hydraulic, for the live steam inlet, with built-in steam strainer

  - 3 Control valves with servo operator for the live steam inlet

  - 5 Bleeds

  - Reverse flow protections for bleeds as shown in P&ID (loose supply)

  - Radial exhaust

  - Control system for speed, power (see chapter 6)

  - Turbine protection (see chapter 6)

  - Mat-type insulation

  - Internal steam pipes with valves for balance piston, sealing steam and leak steam

  - Internal pipes for drain system with valves

  - Internal oil pipes for the lube and control oil system with valves

  - Start-up drains with pneumatic operated shut-off valves

  - Operating drains

  - Baseframe for the turbine

  - Earth terminal

  - Boroscope openings in the turbine casing

  - Sealing steam pressure control (sealing steam from live steam)

  - 1 Connection for air dryer (dehumidifier)

  - 1 Sealing steam cooler for the rear labyrinths

  - Standard preservation (6 months) as per Siemens - factory standard

  - Prime coat and finishing coat of paint as per Siemens - factory standard

  - Touch up paint to Site

  - Operation manual, 3-fold, English langauge

### Steam Turbine – axial exhaust- base offer

1 Condensing turbine type SST 400 comprising:

  - 1 Emergency stop valve, hydraulic, for the live steam inlet, with built-in steam strainer

  - 3 Control valves with servo operator for the live steam inlet

  - 5 Bleeds

  - Reverse flow protections for bleeds as shown in P&ID (loose supply)

  - Axial exhaust

  - Control system for speed, power (see chapter 6)

  - Turbine protection (see chapter 6)

  - Mat-type insulation

  - Internal steam pipes with valves for balance piston, sealing steam and leak steam

  - Internal pipes for drain system with valves

  - Internal oil pipes for the lube and control oil system with valves

  - Start-up drains with pneumatic operated shut-off valves

  - Operating drains

  - Flash box (optional)

  - Baseframe for the turbine

  - Earth terminal

  - Boroscope openings in the turbine casing

  - Sealing steam pressure control (sealing steam from live steam)

  - 1 Connection for air dryer (dehumidifier)

  - 1 Sealing steam cooler for the rear labyrinths

  - Standard preservation (6 months) as per Siemens - factory standard

  - Prime coat and finishing coat of paint as per Siemens - factory standard

  - Touch up paint to Site

  - Operation manual, 3-fold, in English

i

Gear Unit

Single helical high-speed parallel-shaft gear with:

  - Flanges for coupling guard on pinion and gear shaft

  - Hollow shaft between turbine and gear unit

  - Coupling guard between turbine and gear unit

  - Coupling (quillshaft) between gear unit and generator

  - Coupling cover between gear unit and generator

  - Built-on barring gear with electric motor, coupling and softstarter

  - Built-on main oil pump

  - 6 Resistance thermometers wired to terminal box

( 1 x for each radial bearing, 1 x for each side of thrust bearing)

  - Shaft vibration pick-up wired to terminal box

  - Base frame for the gear unit, as oil tank

  - on the base frame are arranged: 1 electrical operated full load standby oil pump, 1 electrical operated emergency oil pump, 1 double oil cooler (2 x 100%), 1 double oil filter (2 x 100%), 1 oil vapour extractor, 1 jacking oil pump

  - Foundation anchors, -bolts and leveling spindles

  - Inspection documents acc. to EN 10204

  - Trial run acc. to the Siemens standard test program

  - Painting acc. to factory standard

  - Preservation acc. to factory standard

### Lube Oil Plant

Design of the oil plant according to the manufacturer's standard Design of the oil coolers according to DIN

The lube oil plant arranged on the gear package with integrated oil tank comprises following main parts:

  - 100% auxiliary oil pump, three-phase a.c. motor driven

  - approx. 40 % emergency oil pump, d.c. motor driven

  - Jacking oil pump, three-phase a.c. motor driven

  - Oil vapor extractor with three-phase a.c. motor

  - Oil tank heater (electric immersion heater for Tamb. < 15°C)

  - 2  x  100  %  oil  coolers  (tubes  made  of  CuZn28Sn  and  tube  sheets  made  of CuZn38SnAlF39)

  - 2 x 100 % lube oil filters

  - Change-over  device  (oil  cooler  and  oil  filter)  for  switching  operations  without interruption of the oil supply

  - Pressure control for the lube oil

  - Oil safety valve

additional accesoires:

  - Direct driven main oil pump (at the gear unit)

### Control Oil Unit

The hydraulic supply unit is installed on a separate skid ready for operation and consists of the following main parts:

  - 2 x 100% displacement piston type pumps, AC motor driven

  - 1 oil tank

  - 1 oil accumulator

  - 2 x 100% oil filter with change over device

  - 1 off-line cooling pump, AC motor driven

  - 1 oil cooler (oil/air) with fan

  - Interconnecting oil pipes (stainless steel) with valves

### Surface Condensing Plant

Not in Siemens’ scope of supply

Optional : Siemens will submit the following documents of the main condenser Incl. in Siemens scope for engineering support is:

    - the thermodynamic design data

based on customer material specification provided in advanced

    - assembly drawing

    - mechanical data sheet including the following.:

    - dimensions of tubes

    - tube sheet

    - shell

    - allocation of tube bundles in tube sheet. Excluded from Siemens scope  is the following :

    - any kind of liability and guarantee

    - support during manufacturing and installation

    - detailed manufacture drawings

    - quality control of manufacture

The design / supply of the ejector unit including condensate pumps, ejectors, inter and after condenser and control valves and interconnecting piping are not in Siemens scope.

### Miscellaneous

ALTERNATIVE 1:

  - Spring elements for the turbine table

  - Basic & detail engineering

  - Documentation in ENGLISH

  - Packing for transportation

  - Freight FOB, north German seaport, in accordance with INCOTERMS 2000

  - Turbine anchor bolts if required by Siemens

Base offer :

  - Basic & detail engineering

  - Documentation in ENGLISH

  - Packing for transportation

  - Freight FOB, north German seaport, in accordance with INCOTERMS 2000

  - Turbine anchor bolts if required by Siemens

  - List of special tools required for erection

Steam turbine

    - Blow out device for trip valve

    - Aligning device (shaft)

    - Container for the special tools

### Spare Parts

One set for two years of continuous operation we recommend the following spare parts:

Steam turbine

- 1 Set of pads for the main bearings of the turbine (radial and axial bearings)

- 1 Set of oil sealing rings for these bearings

- 1 Set of sealing strips with caulking wires for the shaft labyrinths

- 1 Set packings and spindles for control valves

Gear unit

- 1 Set of bearings for the pinion and the wheel shaft

- 1 Set of shaft sealing rings

Oil units

- 1 Set gaskets

- 1 pc. Pressure regulation valve cone

- 1 Set lubrication oil filter elements

- 1 Set control oil filter elements

Instrumentation

- 1 pc. Pick-up for speed

- 1 pc. Pick-up for axial displacement

- 2 pc. Pick-up for shaft vibration

- 2 pc. RTD for bearing temperature – turbine

- 2 pc. RTD for bearing temperature – gear unit

- 1 pc. Pressure switch (valve block)

- 1 pc. Position transducer (steam control valve)

- 2 pc. Instrument 3-way valve

- 1 pc. O-Ring

Generator

Not included in the offer

### Supervison of Erection, commissioning and trial run (separate contract)

The scope of service, based on daily rates, includes the following: The assignment of personnel (and, if applicable, the tools) for:

- the supervision of the erection (ready for commissioning)

- the preparation of commissioning

- the commissioning

- Training on the job during commissioning

- Classroom training (Option), see separate proposal in Ch. 8

- the trial run (3 days, 10 hours daily with recall standby)

- Performance test acc. to ASME PTC 6.1 under conditions specified in section 8.3

An erection / commissioning coordination meeting shall be held before erection & commissioning activities.

See also chapter 8 “Erection time schedule” and "Specification of technical field assistance".

### Performance test acc. ASME PTC 6.1

The turbine unit will be tested in accordance with ASME PTC 6.1 as dicreibed in section 8.03 “conditions for Performance test. The test shall be carried out within three months after the provisional acceptance of the turbine, but no later than six months after first steam to turbine. During the performance test the plant will be operated under the responsibility of the customer taking due account of the operating instructions. The reports on beginning, course and end of the performance tests as issued by the supplier must be signed by the customer.

Performance test will be carried out by third party (not in Siemens scope)

Siemens scope of supply:

Test supervisor Precision instruments

Fitting and removal of Siemens’s precision instruments

Performances by others:

Labour, normal operating personnel, helpers etc. Nozzles for flow measurements

Calibrated measuring transformers (3-phase) for power measurement Necessary pressure taps outside Siemens delivery limits

Necessary temperature pockets outside Siemens delivery limits

Duration:

Three up to five days for the installation of Siemens-measuring instruments. Two days each loadpoint for the calibration and testing.

If the test should be delayed due to reasons beyond Siemens control, any additional cost for Siemens personnel and instruments will be charged.

Number of test points:

The performance test will be carried out for one load point.

Tolerances:

The tolerances which are mentioned in the test instructions will be applied.

i

Exclusions from our Scope of Supply and Services

Steam Turboset

The following components and services are not included in our scope of supply:

- Live steam pipe up to the live-steam emergency-stop valve

- Condenser and Condensing system components

- Spacer / Interconnecting piece Turbine – main condenser

- Condensate sampeling / analysing system

- Tube cleaning system of main condenser

- Bleed steam pipes from turbine nozzle to the bleed non-return flap valve and from there to the bleed steam system

- Cooling water pipes with isolating valves to and from the connecting nozzles

of the corresponding equipment

- Safety valves in the steam, bleed, and water pipes

- Electric cables, switches, contactors and fuses

- Foundations, earthworks, soil preparation

- Spring elements (not required in case of base offer)

- Dehumidifier

- Grouting of baseframe with non shrinking material

- Masonry

- Heating and lighting of the machine house

- Compressed air, water and power supply on site

- Shop test run

- Manufacturing drawings

- Guarantee measurements

- Machine house crane

- Steel structures, platforms, pedestals

- Auxiliary systems, such as cooling water circuit etc.

- HP and LP bypass stations

- Lightning protection and earthing system

- Fire fighting equipment

- First oil filling

- Calculation of the foundation

- Noise hood or Hood for outdoor installation

- Generator and accessories (only one generator is included for Turbine 1)

- Pressure reducing or by pass station

- Interconnecting oil piping between oil system and Generator

- Vent steam condenser

General remark:

All systems connected to the turbine have to be self-protected in acc. with DGRL 9723EG

### Limits of Supply

Steam

Inlet connection of the turbine live-steam emergency-trip valve Outlet flanges of the turbine bleeds

Inlet and outlet flanges of the bleed non-return flap valves Outlet connection on turbine exhaust

Inlet flanges of the sealing steam pressure control valves

Cooling Water

Inlet and outlet flanges of the oil coolers

Inlet and outlet flanges of the generator (only in case generator is in Siemens scope of supply)

Drains

Outlet flange of the falsh box

Electric Current

Connecting terminals of the electric motors Connecting terminals of the solenoid valves

Connecting terminals for terminal strip (group terminal) Connecting terminals inside the cubicles

Oil

Filling connection on turbine oil tank

Inlet / Outlet flange on oil reservoir to the generator (both lubricating oil & lifting oil)

Air (Compressed Air and Instrument Air)

Connection at the control equipment

General remark:

In general the piping interface to customer shall be according to Siemens standard i.e. welding or Flanges. In case of Flanges it shall be according to ANSI. Counter flanges, bolts and interconnecting piececs will be supplied by Kaidi.

Siemens will submit during detailed engineering a detailed list, including detailed flange, bolts, nuts,gaskets…etc informations, of all customer’s connections.

For further details please refer to attached P&I Diagrams in Chaper 7

Limits of Supply

To define the limits of supply the following symbol is used in the P&I diagrams: (see chapter 7)

S C

Customer/Others Siemens

### Standards, Regulations and Guidelines

The applicable standards, regulations and guidelines valid at the time of tender submission form the basis for planning and supply of the equipment, except for deviations that are specified in the list of deviations and clarifications.

Unless otherwise agreed, we use the power system designation system KKS, last edition. In respect of numbering, a more detailed system incorporating suitable producer-related groups of numbers is employed in addition.

Basic Standards

Unless other basic standards have been agreed upon with the customer, the quotation of SIEMENS is based on European standards and international standards (EN, DIN, IEC etc.) and the following standards, as far as the equipment covered therein is part of the scope of supply:

Main Components

- Turbine with pressure casing and pressure oil system acc. to DIN 4312.

- Gear units acc. to AGMA 421.06

- Generator acc. to European IEC-Standards

- Condenser: mechanical strength acc. to AD-regulations, bases on VGB-R455P, thermal rating acc. to HEI.

Pipes and Connections

- Internal design of steam and condensate pipes acc. to DIN 2413.

- Oil pipes made of stainless steel, seam welded

- Flanged connections in the oil system PN16 acc. to DIN EN 1092-1, contact surface acc. to Form B.

- Flanged connections in the steam area acc. to DIN EN 1092-1

Plant Control and Instrumentation

- Vibration severity acc. to ISO 10816, shaft vibrations acc. to ISO 7919.

Probes acc. to DIN 43 760.

Protection

- Earthing acc. to VDE 0100 and 0141, identification acc. to DIN 40 011.

Inspection and Testing

- Examinations and tests according to the E&T Plan of SIEMENS. Certificates acc. to EN 10 204-2.2 and 3.1.

- The thermal acceptance tests of steam turbines are performed acc. to DIN 1943. (VDI-Steam Turbine Code)

- Examination and acceptance of pipes and connections acc. to DIN EN 1127.

- Non destructive tests acc. to DIN EN 1559

- Qualification testing of welders acc. to DIN-EN 287.

Welding

- Welding procedure acc. to DIN EN 15614.

Noise

- Sound measurement acc. to EN ISO 4871.

Insulation

- The insulation thickness is determined in accordance with our factory standard based on DIN 18 421 and VDI 2065. Material certificate acc. to VDI 2055.

Painting / Preservation

- De-rusting in accordance with the Swedish standard SA 2,5, similar as DIN 55928.

- Prime coat of paint acc. to manufacturer‘s standard.

- Final painting acc. to manufacturer‘s standard.

- Preservation	for	non-painted	surfaces	acc.	to	manufacturer‘s	standard	in accordance with VGB-R 116 H.

Electrical Systems

- Electric motors: Rating classes acc. to IEC 34. Standard motors acc. to IEC 72 and DIN 42 677.

- Cables for voltages up to 60 V acc. to VDE 0815.

Miscellaneous

- Turbine oil acc. to ISO, viscosity VG 46.

- Material strength design of the heat exchangers acc. to AD-Code of Practice, DIN materials acc. to VGB-R455P table 3.

- Deviations and tolerances for tube bundles and heat exchangers acc. to DIN 28 008.

- Design of steam ejectors and vacuum pumps acc. to VGB-R 126 L.

- Bolts acc. to DIN 933, nuts acc. to DIN 934. Bolted joints on pressure casings acc. to DIN 938/939. Admissible stresses in the bolts acc. to DIN ISO 898 / DIN 17240, in the nuts acc. to DIN 267.

- Denominations acc. to DIN 19 227 in accordance with SI basic units acc. to DIN 1301.

- Symbols on P&I D`s acc. to ISO 10628.

- Blowing  out  of  steam  piping  in  accordance  with  Siemens  factory  standard 1CWN002896.

### Technical Requirements

Oil Specification

For the common lube and control oil system for turbine, gearing (if applicable) and driven unit, mineral oil must be used  in  accordance  with  DIN  Standard  51515 (May 1978) and have the following properties:.

Designation                                Requirement                               Test Method

Lube oil type                                  TD 46

ISO viscosity class                         ISO VG 46                                   DIN 51519

Hitherto           existing           code 	25

number (correlation)

Kinematic viscosity at 40°C           min. 41.4      mm2/ s (cSt)           DIN 51550

max. 50.6	mm2/ s (cSt)	in connection with

DIN 51561 or

DIN 51562

Mean dynamic viscosity at 40°C	41.4 x 10-3	Pa s

Viscosity index not less than	95

Density at 15°C not more than	0.90	kg/l	DIN 51757 Flash point (Cleveland)

not less than	185	°C	DIN 51376

Pourpoint equal to or less than	-6	°C	DIN 51597

Neutralisation number	DIN 51558

not more than	0.1 *)	mgKOH/g	Part 1 Max. saponification number	0.15 *)	mgKOG/g	DIN 51559

Max. ash content (oxide ash)

not more than	0.01 *)	% by weight

Water content	g/100g	below the limit of quantifiable

detectability	DIN 51582

| Content of foreign solids | below the limit of quantifiable |  |
| --- | --- | --- |
| g/100g | detectability | DIN 51592 |

| Designation Demulsification number | Requirement max. 300 | sec. | Test Method DIN 51589 |
| --- | --- | --- | --- |
|  |  |  | Part 1 |
| De-airability (air release property) at 50°C | max. 5 | min | DIN 51581 |
| Corrosion influence on copper, |  |  | DIN 51759 |
| corrosion degree | max. 2-100 A3 |  | (3h at 100°C) |
| Corrosion protection property against steel | 0 - A (free of corrosion) |  | DIN 51585 |
| Ageing behaviour Increase of neutralisation number after 1000 h | max.2.0 mg KOH / g oil |  | DIN 51587 |
| Spec. loadability (gear unit) | 6 - 7 Damage power stage **) FZG Normal test IP 166/65 |  | DIN 51354 (A/8, 3/90) ASTM D 1976 |

*)	As additives are used, these values are higher and are to be stated by the supplier.

Oils with additive materials contain deterioration and corrosion protection as well as additive which prevent foaming.

NOTE:

EP additives increase the specific loadability (mechanical limiting load)

- with EP additives (FZG >7):	turbosets with gear units

- without EP additives(FZG <7):	turbosets without gear units

Refer to the lube oil specification of the gear manufacturer in this regard.

**)	Not included in DIN 51515.

Steam purity requirements

Guidelines for the inlet steam condensate

Kindly refer to the attachment, 02_Appendix_2.3_Steam_Purity_Requirement.pdf, for the recommended steam quality.

Monitoring

We strongly recommend the continous monitoring of the water/steam cycle by constantly recording the electric conductivity (at 25 °C) at a local sampling point downstream of the strongly acidic cation exchanger, and the determination of the silicia content. The monitoring equipment should be installed on the inlet steam and condensate sides.

### Genral Comments on Technical Inquiry Specifications

Our supplies and services shall be designed in accordance with those standards, guidelines and specifications applicable within Germany and Europe. The customer’s piping interface will be ANSI flange connections . In addition, Siemens has developed internal guidelines and specifications for implementation, based on its many years of experience	with          steam          turbine           generation           plants. This ensures a high degree of safety and availability.

### List of Major Suppliers for Equipment for Turbogroups

Siemens cooperates with approved suppliers and procures equipment and materials world wide at competitive price levels. It is not possible therefore to name single subcontractors for the various items of the power plant.

The subsuppliers are approved by Siemens. Siemens may also consider other equivalent approved suppliers and reserves the right to select an equivalent supplier.

Kindly refer to 02_Appendix_2.2_Siemens_Subsuppliers_List.pdf for the list of sub- suppliers.

Ka

Exhaust pressure limit graph	Z7

FOR CONSTRUCTION

0,3

0,28

0,26

0,24

0,22

0,2

Max. perm. Exhaust pressure [bar]

0,18

0,16

0,14

Valid for: po=128 bar

o

0,12

to=535  C

30

speed 5500 rpm

0,1

0,08

0,06

0,04

0,02

0

5

10

15

20

25

0

Date:8.11.2011,rev1	Worked by: Hlka

Exhaust Steam Flow [kg/s]

FOR CONSTRUCTION

Main Control Valves Characteristic

K DZ8

140000

130000

120000

Valid for: po=128 bar a to=535 °C

pE=10 bar a

110000

100000

90000

mo  - Inlet Steam Flow

[kg/h]

80000

70000

60000

50000

40000

30000

20000

10000

0

5

10

15

20

25

30

35

0

Date:8.11.2011,rev1	Calculated by: Holka

valves hub [mm]

FOR CONSTRUCTION

Minimal  Inlet Steam Temperature

Ka Z10

300

275

250

225

200

175

150

600

550

500

Turbine nominal parameters:

po=128 bar (a)

o

450

to=535  C

o

to  - Inlet Steam Temperature [ C]

400

350

Minimum initial inlet steam parameters for speeding po=25 bar (a)

o

to=275  C

300

Operational inlet steam pressure according diagram 5782-98 5807-16/DZ9

250

125

200

100

mo - Inlet Steam Flow [t/h]

150	75

100	50

50	25

0

5

10

15

20

25

30

35

40

45

50

55

60

65

70

0	0

Worked bya

Date:8.11.2011,Rev1

pz - Wheel Chamber Pressure [bar (abs)]

FOR CONSTRUCTION

Permissible Inlet	Ka

Steam Parameters	2

570

560

Operation outside of areas A,B,C is not permitted ! Not for Sliding Operation!

550

540	B	A

530

520

510

o

to  - Intet Steam Temperature [  C ]

C

500

490

480

Rated Parameters: 128 bar/535 oC

470

460

450

440

IAEC- F4o5r-1Continuous Operation B - Time Limited

C - For speeding and loading up to minimal output

430

420

410

64

70

76

82

88

94

100

106

112

118

124

130

136

142

400

po - Inlet Steam Pressure [ bar ]

Date: 8.11.2011,rev1	Calculated by: Hlka

FOR CONSTRUCTION

Turbine output versus	Ka

exhaust pressure	11

1,01

1

0,99

Valid for: po=128 bar

o

to=535  C

P/Pmax [1]

0,98

condensing mode regeneration in operation 120 t/h, Pmax=30 MW 90t/h, Pmax=22.2 MW

0,14

0,97

0,96

0,95

0

0,01

0,02

0,03

0,04

0,05

0,06

0,07

0,08

0,09

0,1

0,11

0,12

0,13

0,94

p  - exhaust pressure [bar]

Date:8.11.2011, rev0	Worked by:ka

k

FOR CONSTRUCTION

##### Inlet Steam Pressure vs Inlet Steam Flow	Ka 9

135

130

125

120

115

110

105

100

95

Inlet steam pressure [bar]

90

85

80

75

70

65

60

55

50

45

40

35

30

25

20

15

10

5

0

5

10

15

0

Valid for :

inlet steam temperature according 5782-98 5807-16/DZ10

0,0; 51,2

48,0; 51,2

120,0; 128,0

20

25

30

35

40

45

50

55

60

65

70

75

80

85

90

95

100

105

110

115

120

125

130

Date:8.11.2011,rev1

Inlet steam flow [t/h]

Calculated by:Hlka

140

FOR CONSTRUCTION

##### Informative Turbine Charakteristic		K Z6

130

Valid for :

inlet pressure - po = 128 bar

o

inlet temperature - to = 535  C

120

110

100

extraction pressure - pE = 10 bar cooling water temp. - tW = 25 °C cooling water flow - mW = 4130 t/h speed - n = 5000 r.p.m. regeneration in operation

all pressures are absolute!

mo - Inlet Steam Flow [t/h]

90

Example :

80	inlet steam flow - mo = 87 t/h

process steam - mE = 20 t/h

70	output at gen. terminals - PG = 18.7 MW

60	po,to,mo

50

40

30	PG

20

n

mHPH2 mHPH1

mDeaerator

mLPH2

mLPH1

pE,mE

tw,mw

10

0

1

2

3

4

5

6

7

8

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

26

27

28

29

30

31

32

33

34

35

0

Date:8.11.2011, rev.1

PG - Output at Generator Terminals [MW]

Calculated by:Homolka

FOR CONSTRUCTION

Wheel Chamber Pressure

K

/DZ3

130

75

70

Valid for: po=128 bar (a)

65	o

to=535  C

pE=10 bar (a)

60	regeneration in operation

55

pz-wheel chamber pressure [bar(a)]

50

45

40

35

30

25

20

15

10

5

0

10

20

30

40

50

60

70

80

90

0

100

110

120

Date:8.11.2011,rev1	Worked by:Hoa

mo-Inlet Steam Flow [t/h]

|  |  |  |  |  |  |  |  |  |  |  |  |  |  | K |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | B |  | 128.00 3432.4 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5782-5798, 5807-5816/DZ1 |  |  |  |
|  |  |  | DP = 2.000 bar |  |  |  |  | 535.0 31.98 |  |  |  |  |  |  |  |  |  |
| 130.00 3438.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | DT = 3.00 C |  |  |  |  |  |  |  |  |  |  | Output at exit flange gearbox = 30480 kW |  |  |  |
| 538.0 32.04 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | A |  |  | 128.00 | 3432.4 |  | 128.00 3432.4 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 535.0 | 0.100 |  | 535.0 31.88 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Sealing | steam |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | G 30000 kW |  |  |  |
| --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 159.00 | 1026.4 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 237.2 | 32.04 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | B |  |  |  |
|  |  |  |  | 33.002 3153.0 |  |  |  |  |  | 34.377 | 3153.0 |  |  |  |  |  |  |
|  |  |  |  | 367.7 2.047 |  |  |  |  |  | 368.9 | 2.047 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 0.068 | 2261.5 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 38.50 | 21.82 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 18.856 3014.9 |  |  |  |  |  |  |
| 33.002 899.99 | 159.50 | 882.46 |  |  |  |  |  |  |  |  |  |  |  | C |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 294.3 1.52 | 4 |  |  |  |  |  |
| 210.4 2.047 | 205.4 | 32.04 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 18.102 3014.9 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 293.3 1.524 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- A |  |  |  |
|  | 160.00 | 768.86 |  |  |  |  |  |  |  |  |  |  |  | to Process |  |  |  |
|  |  |  |  | --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 179.5 | 32.04 |  |  |  |  |  | C |  |  |  |  |  |  |  |  |  |
|  |  |  |  | --- --- |  |  |  |  |  |  | 10.000 | 2891.1 | 0.068 | 2261.5 128.00 3432.4 |  |  |  |
| 18.102 783.45 |  |  |  |  |  |  |  |  |  |  | 227.1 | 2.029 | 38.50 | 21.82 535.0 0.060 |  |  |  |
| 184.5 3.571 |  |  |  |  |  |  |  |  |  |  |  |  |  | SJAE |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 9.250 | 747.79 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 176.5 | 32.04 |  |  |  |  |  |  |  |  |  |  |  | 3.000 105.04 |  |  |  |
|  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 25.00 1103.2 |  |  |  |
|  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 9.500 2891.1 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2.300 146.82 |  |  |  |
|  |  |  |  | 226.1 2.029 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 35.02 1103.2 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 0.068 | 161.18 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 3.811 2731.3 |  |  |  |  |  |  |
|  | 9.500 | 578.51 |  |  |  |  |  |  |  |  |  |  | 38.50 | 26.44 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 141.9 2.172 |  |  |  |  |  |  |
|  | 137.4 | 26.44 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 3.659 2731.3 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 140.4 2.172 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 11.000 | 162.76 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 38.64 | 26.44 |  |  |  |
| 3.659 412.84 | 10.000 | 388.07 |  |  |  |  |  | 0.896 2530.9 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 2.000 125.84 |  |  |  |  |  |  |
| 98.48 2.172 | 92.48 | 26.44 |  |  |  |  |  | 96.59 2.29 | 2 |  |  |  |  |  |  |  |  |
|  |  |  |  | 0.860 2530.9 |  |  |  |  |  |  | 30.00 0.055 |  |  |  |  |  |  |
|  |  |  |  | 95.48 2.292 |  |  |  |  |  |  | Make-up water |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | Return water from process |  |  |  |
|  |  |  |  | 0.860 191.26 |  |  |  |  |  |  |  |  |  | FOR CONSTRUCTION |  |  |  |
| 10.500 167.04 45.68 4.464 |  |  |  |  |  |  |  |  |  |  |  |  | Hom 5.12.11,Rev4 |  | E O IP SL P SU | HEAT BALANCE DIAGRAM | 12 |
| 39.68 26.44 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| p [bar] h [kJ/kg] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LP: THA - CW=25°C |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SIEMENS AG Energy Sector |  |  |  |  |
| t [°C] m [kg/s] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | n | 1 |
| C:\Da.kgr |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  | Guaranteed Operation Conditions K III , IV |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | B |  | 128.00 3432.4 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 5782-5798, 5807-5816/DZ1 |  |  |  |  |
|  |  |  | DP = 2.000 bar |  |  |  |  | 535.0 33.27 |  |  |  |  |  |  |  |  |  |
| 130.00 3438.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | DT = 3.00 C |  |  |  |  |  |  |  |  |  | Output at exit flange gearbox = 31737 kW |  |  |  |  |
| 538.0 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | A |  |  | 128.00 | 3432.4 |  | 128.00 3432.4 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 535.0 | 0.100 |  | 535.0 33.17 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Sealing | steam |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | G 31230 kW |  |  |  |  |
| --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 159.00 | 1027.8 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 237.5 | 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | B |  |  |  |  |
|  |  |  |  | 33.324 3153.8 |  |  |  |  |  | 34.713 | 3153.8 |  |  |  |  |  |  |
|  |  |  |  | 368.4 2.131 |  |  |  |  |  | 369.5 | 2.131 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 0.068 2262.2 |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 38.60 22.68 |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 19.046 3016.2 |  |  |  |  |  |  |
| 33.324 902.01 | 159.50 | 883.80 |  |  |  |  |  |  |  |  |  |  | C |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 295.0 1.60 | 4 |  |  |  |  |  |
| 210.8 2.131 | 205.7 | 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 18.285 3016.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 294.1 1.604 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- A |  |  |  |  |
|  | 160.00 | 768.86 |  |  |  |  |  |  |  |  |  |  | to Process |  |  |  |  |
|  |  |  |  | --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 179.5 | 33.33 |  |  |  |  |  | C |  |  |  |  |  |  |  |  |  |
|  |  |  |  | --- --- |  |  |  |  |  |  | 10.000 | 2890.9 | 0.068 2262.2 128.00 3432.4 |  |  |  |  |
| 18.285 784.34 |  |  |  |  |  |  |  |  |  |  | 227.0 | 2.098 | 38.60 22.68 535.0 0.060 |  |  |  |  |
| 184.7 3.735 |  |  |  |  |  |  |  |  |  |  |  |  | SJAE |  |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 9.250 | 747.79 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 176.5 | 33.33 |  |  |  |  |  |  |  |  |  |  | 3.000 105.04 |  |  |  |  |
|  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 25.00 1149.9 |  |  |  |  |
|  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 9.500 2890.9 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 2.300 146.72 |  |  |  |  |
|  |  |  |  | 226.0 2.098 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 34.99 1149.9 |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 0.068 161.60 |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 3.851 2728.1 |  |  |  |  |  |  |
|  | 9.500 | 579.36 |  |  |  |  |  |  |  |  |  |  | 38.60 27.50 |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 142.3 2.263 |  |  |  |  |  |  |
|  | 137.6 | 27.50 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 3.697 2728.1 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 140.8 2.263 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 11.000 163.18 |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 38.74 27.50 |  |  |  |  |
| 3.697 414.41 | 10.000 | 388.96 |  |  |  |  |  | 0.909 2528.4 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 2.000 125.84 |  |  |  |  |  |  |
| 98.85 2.263 | 92.69 | 27.50 |  |  |  |  |  | 96.99 2.39 | 4 |  |  |  |  |  |  |  |  |
|  |  |  |  | 0.873 2528.4 |  |  |  |  |  |  | 30.00 0.055 |  |  |  |  |  |  |
|  |  |  |  | 95.87 2.394 |  |  |  |  |  |  | Make-up water |  | --- --- |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | Return water from process |  |  |  |  |
|  |  |  |  | 0.873 192.28 |  |  |  |  |  |  |  |  | FOR CONSTRUCTION |  |  |  |  |
| 10.500 167.30 45.92 4.657 |  |  |  |  |  |  |  |  |  |  |  |  |  | Hom 5.12.11,Rev4 | E O IP SL P SU | HEAT BALANCE DIAGRAM | 12 |
| 39.74 27.50 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| p [bar] h [kJ/kg] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LP: THA - CW=25°C |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | SIEMENS AG Energy Sector |  |  |  |
| t [°C] m [kg/s] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | n | 2 |
| C:\Data3.kgr |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  | K III , IV |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | B |  | 128.00 3432.4 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5782-5798, 5807-5816/DZ1 |  |  |  |
|  |  |  | DP = 2.000 bar |  |  |  |  | 535.0 32.36 |  |  |  |  |  |  |  |  |  |
| 130.00 3438.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | DT = 3.00 C |  |  |  |  |  |  |  |  |  |  | Output at exit flange gearbox = 30480 kW |  |  |  |
| 538.0 32.42 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | A |  |  | 128.00 | 3432.4 |  | 128.00 3432.4 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 535.0 | 0.100 |  | 535.0 32.26 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Sealing | steam |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | G 30000 kW |  |  |  |
| 159.00 1646.6 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 159.00 | 1022.5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 346.8 1.000 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 236.3 | 33.42 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | B |  |  |  |
|  |  |  |  | 32.580 3162.8 |  |  |  |  |  | 33.938 | 3162.8 |  |  |  |  |  |  |
|  |  |  |  | 371.6 2.093 |  |  |  |  |  | 372.7 | 2.093 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 0.102 | 2289.0 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 46.30 | 22.17 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 18.721 3025.3 |  |  |  |  |  |  |
| 32.580 898.17 | 159.50 | 880.65 |  |  |  |  |  |  |  |  |  |  |  | C |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 298.6 1.55 | 9 |  |  |  |  |  |
| 210.0 2.093 | 205.0 | 33.42 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 17.972 3025.3 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 297.6 1.559 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- A |  |  |  |
|  | 160.00 | 768.86 |  |  |  |  |  |  |  |  |  |  |  | to Process |  |  |  |
|  |  |  |  | --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 179.5 | 33.42 |  |  |  |  |  | C |  |  |  |  |  |  |  |  |  |
|  |  |  |  | --- --- |  |  |  |  |  |  | 10.000 | 2901.9 | 0.102 | 2289.0 128.00 3432.4 |  |  |  |
| 17.972 783.35 |  |  |  |  |  |  |  |  |  |  | 231.8 | 2.171 | 46.30 | 22.17 535.0 0.060 |  |  |  |
| 184.5 3.652 |  |  |  |  |  |  |  |  |  |  |  |  |  | SJAE |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 9.250 | 747.79 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 176.5 | 33.42 |  |  |  |  |  |  |  |  |  |  |  | 3.000 138.47 |  |  |  |
|  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 33.00 1103.2 |  |  |  |
|  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 9.500 2901.9 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2.300 180.73 |  |  |  |
|  |  |  |  | 230.8 2.171 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 43.13 1103.2 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 0.102 | 193.79 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 3.725 2736.2 |  |  |  |  |  |  |
|  | 9.500 | 573.63 |  |  |  |  |  |  |  |  |  |  | 46.30 | 27.60 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 141.8 2.192 |  |  |  |  |  |  |
|  | 136.3 | 27.60 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 3.576 2736.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 141.2 2.192 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 11.000 | 195.37 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 46.45 | 27.60 |  |  |  |
| 3.576 413.50 | 10.000 | 389.18 |  |  |  |  |  | 0.890 2536.9 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 2.000 125.84 |  |  |  |  |  |  |
| 98.63 2.192 | 92.74 | 27.60 |  |  |  |  |  | 96.42 2.07 | 5 |  |  |  |  |  |  |  |  |
|  |  |  |  | 0.855 2536.9 |  |  |  |  |  |  | 30.00 1.055 |  |  |  |  |  |  |
|  |  |  |  | 95.30 2.075 |  |  |  |  |  |  | Make-up water |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | Return water from process |  |  |  |
|  |  |  |  | 0.855 218.86 |  |  |  |  |  |  |  |  |  | FOR CONSTRUCTION |  |  |  |
| 10.500 199.43 52.28 4.267 |  |  |  |  |  |  |  |  |  |  |  |  | Hom 5.12.11,Rev4 |  | E O IP SL P SU | HEAT BALANCE DIAGRAM | 12 |
| 47.43 27.60 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| p [bar] h [kJ/kg] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LP: TRL - CW=33°C |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SIEMENS AG Energy Sector |  |  |  |  |
| t [°C] m [kg/s] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | K | 3 |
| C:\Datagr |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  | K III , IV |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | B |  | 128.00 3432.4 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5782-5798, 5807-5816/DZ1 |  |  |  |
|  |  |  | DP = 2.000 bar |  |  |  |  | 535.0 33.27 |  |  |  |  |  |  |  |  |  |
| 130.00 3438.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | DT = 3.00 C |  |  |  |  |  |  |  |  |  |  | Output at exit flange gearbox = 31788 kW |  |  |  |
| 538.0 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | A |  |  | 128.00 | 3432.4 |  | 128.00 3432.4 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 535.0 | 0.100 |  | 535.0 33.17 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Sealing | steam |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | G 31290 kW |  |  |  |
| --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 159.00 | 1029.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 237.8 | 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | B |  |  |  |
|  |  |  |  | 33.424 3163.4 |  |  |  |  |  | 34.817 | 3163.4 |  |  |  |  |  |  |
|  |  |  |  | 372.5 2.132 |  |  |  |  |  | 373.7 | 2.132 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 0.070 | 2269.7 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 39.09 | 22.71 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 19.084 3024.5 |  |  |  |  |  |  |
| 33.424 902.80 | 159.50 | 884.58 |  |  |  |  |  |  |  |  |  |  |  | C |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 298.6 1.60 | 9 |  |  |  |  |  |
| 211.0 2.132 | 205.9 | 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 18.321 3024.5 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 297.7 1.609 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- A |  |  |  |
|  | 160.00 | 768.86 |  |  |  |  |  |  |  |  |  |  |  | to Process |  |  |  |
|  |  |  |  | --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 179.5 | 33.33 |  |  |  |  |  | C |  |  |  |  |  |  |  |  |  |
|  |  |  |  | --- --- |  |  |  |  |  |  | 10.000 | 2898.0 | 0.070 | 2269.7 128.00 3432.4 |  |  |  |
| 18.321 784.43 |  |  |  |  |  |  |  |  |  |  | 230.1 | 2.087 | 39.09 | 22.71 535.0 0.060 |  |  |  |
| 184.7 3.742 |  |  |  |  |  |  |  |  |  |  |  |  |  | SJAE |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 9.250 | 747.79 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 176.5 | 33.33 |  |  |  |  |  |  |  |  |  |  |  | 3.000 105.04 |  |  |  |
|  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 25.00 1103.2 |  |  |  |
|  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 9.500 2898.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2.300 148.65 |  |  |  |
|  |  |  |  | 229.1 2.087 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 35.45 1103.2 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 0.070 | 163.66 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 3.857 2734.4 |  |  |  |  |  |  |
|  | 9.500 | 579.63 |  |  |  |  |  |  |  |  |  |  | 39.09 | 27.50 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 142.3 2.256 |  |  |  |  |  |  |
|  | 137.7 | 27.50 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 3.702 2734.4 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 141.0 2.256 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 11.000 | 165.23 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 39.24 | 27.50 |  |  |  |
| 3.702 414.73 | 10.000 | 389.38 |  |  |  |  |  | 0.911 2533.7 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 2.000 125.84 |  |  |  |  |  |  |
| 98.92 2.256 | 92.79 | 27.50 |  |  |  |  |  | 97.05 2.37 | 4 |  |  |  |  |  |  |  |  |
|  |  |  |  | 0.875 2533.7 |  |  |  |  |  |  | 30.00 0.055 |  |  |  |  |  |  |
|  |  |  |  | 95.93 2.374 |  |  |  |  |  |  | Make-up water |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | Return water from process |  |  |  |
|  |  |  |  | 0.875 193.96 |  |  |  |  |  |  |  |  |  | FOR CONSTRUCTION |  |  |  |
| 10.500 169.35 46.33 4.629 |  |  |  |  |  |  |  |  |  |  |  |  | Hom 5.12.11,Rev4 |  | E O IP SL P SU | HEAT BALANCE DIAGRAM | 12 |
| 40.23 27.50 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| p [bar] h [kJ/kg] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LP: VWO - CW=25°C |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SIEMENS AG Energy Sector |  |  |  |  |
| t [°C] m [kg/s] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | n | 4 |
| C:\Dkgr |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | K III , IV |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | B |  | 128.00 3432.4 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5782-5798, 5807-5816/DZ1 |  |  |  |
|  |  |  | DP = 2.000 bar |  |  |  |  |  | 535.0 33.27 |  |  |  |  |  |  |  |  |  |
| 130.00 3438.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | DT = 3.00 C |  |  |  |  |  |  |  |  |  |  |  | Output at exit flange gearbox = 29988 kW |  |  |  |
| 538.0 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | A |  |  | 128.00 | 3432.4 |  | 128.00 3432.4 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | 535.0 | 0.100 |  | 535.0 33.17 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Sealing | steam |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | G 29520 kW |  |  |  |
| --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 159.00 | 1029.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 237.8 | 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | B |  |  |  |
|  |  |  |  | 33.425 | 3163.4 |  |  |  |  |  | 34.817 | 3163.4 |  |  |  |  |  |  |
|  |  |  |  | 372.5 | 2.132 |  |  |  |  |  | 373.7 | 2.132 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.064 | 2264.5 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 37.34 | 19.86 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | 19.085 3024.5 |  |  |  |  |  |  |
| 33.425 902.80 | 159.50 | 884.59 |  |  |  |  |  |  |  |  |  |  |  |  | C |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | 298.6 1.60 | 9 |  |  |  |  |  |
| 211.0 2.132 | 205.9 | 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 18.321 | 3024.5 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 297.7 | 1.609 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 10.000 2898.0 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 230.1 2.778 A |  |  |  |
|  | 160.00 | 768.86 |  |  |  |  |  |  |  |  |  |  |  |  | to Process |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 179.5 | 33.33 |  |  |  |  |  |  | C |  |  |  |  |  |  |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  | 10.000 | 2898.0 | 0.064 | 2264.5 128.00 3432.4 |  |  |  |
| 18.321 784.44 |  |  |  |  |  |  |  |  |  |  |  | 230.1 | 2.314 | 37.34 | 19.86 535.0 0.060 |  |  |  |
| 184.7 3.742 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SJAE |  |  |  |
|  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 9.250 | 747.79 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 176.5 | 33.33 |  |  |  |  |  |  |  |  |  |  |  |  | 3.000 105.04 |  |  |  |
|  |  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 25.00 1103.2 |  |  |  |
|  |  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 9.500 | 2898.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2.300 143.22 |  |  |  |
|  |  |  |  | 229.1 | 2.314 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 34.15 1103.2 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.064 | 156.32 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | 3.388 2729.6 |  |  |  |  |  |  |
|  | 9.500 | 560.38 |  |  |  |  |  |  |  |  |  |  |  | 37.34 | 24.50 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | 137.7 2.186 |  |  |  |  |  |  |
|  | 133.2 | 27.28 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 3.253 | 2729.6 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 136.9 | 2.186 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 11.000 | 157.90 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 37.48 | 24.50 |  |  |  |
| 3.253 398.63 | 10.000 | 373.55 |  |  |  |  |  |  | 0.793 2530.7 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | 2.000 125.84 |  |  |  |  |  |  |
| 95.11 2.186 | 89.02 | 27.28 |  |  |  |  |  |  | 93.29 2.29 | 4 |  |  |  |  |  |  |  |  |
|  |  |  |  | 0.762 | 2530.7 |  |  |  |  |  |  | 30.00 0.055 |  |  |  |  |  |  |
|  |  |  |  | 92.20 | 2.294 |  |  |  |  |  |  | Make-up water |  |  | 9.000 126.48 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 30.00 2.778 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Return water from process |  |  |  |
|  |  |  |  | 0.762 | 183.19 |  |  |  |  |  |  |  |  |  | FOR CONSTRUCTION |  |  |  |
| 10.500 158.85 43.75 4.480 |  |  |  |  |  |  |  |  |  |  |  |  |  | Hom 5.12.11,Rev4 |  | E O IP SL P SU | HEAT BALANCE DIAGRAM | 12 |
| 37.72 27.28 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| p [bar] h [kJ/kg] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LP: 10t/h Process - CW=25°C |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | SIEMENS AG Energy Sector |  |  |  |  |
| t [°C] m [kg/s] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | n | 5 |
| C:\D.kgr |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | K III , IV |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | B |  | 128.00 3432.4 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5782-5798, 5807-5816/DZ1 |  |  |  |
|  |  |  | DP = 2.000 bar |  |  |  |  |  | 535.0 33.27 |  |  |  |  |  |  |  |  |  |
| 130.00 3438.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | DT = 3.00 C |  |  |  |  |  |  |  |  |  |  |  | Output at exit flange gearbox = 28138 kW |  |  |  |
| 538.0 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | A |  |  | 128.00 | 3432.4 |  | 128.00 3432.4 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | 535.0 | 0.100 |  | 535.0 33.17 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Sealing | steam |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | G 27700 kW |  |  |  |
| --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 159.00 | 1029.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 237.8 | 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | B |  |  |  |
|  |  |  |  | 33.424 | 3163.4 |  |  |  |  |  | 34.817 | 3163.4 |  |  |  |  |  |  |
|  |  |  |  | 372.5 | 2.132 |  |  |  |  |  | 373.7 | 2.132 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.058 | 2267.3 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 35.68 | 17.03 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | 19.084 3024.5 |  |  |  |  |  |  |
| 33.424 902.80 | 159.50 | 884.58 |  |  |  |  |  |  |  |  |  |  |  |  | C |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | 298.6 1.60 | 9 |  |  |  |  |  |
| 211.0 2.132 | 205.9 | 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 18.321 | 3024.5 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 297.7 | 1.609 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 10.000 2898.0 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 230.1 5.556 A |  |  |  |
|  | 160.00 | 768.86 |  |  |  |  |  |  |  |  |  |  |  |  | to Process |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 179.5 | 33.33 |  |  |  |  |  |  | C |  |  |  |  |  |  |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  | 10.000 | 2898.0 | 0.058 | 2267.3 128.00 3432.4 |  |  |  |
| 18.321 784.43 |  |  |  |  |  |  |  |  |  |  |  | 230.1 | 2.581 | 35.68 | 17.03 535.0 0.060 |  |  |  |
| 184.7 3.742 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SJAE |  |  |  |
|  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 9.250 | 747.79 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 176.5 | 33.33 |  |  |  |  |  |  |  |  |  |  |  |  | 3.000 105.04 |  |  |  |
|  |  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 25.00 1103.2 |  |  |  |
|  |  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 9.500 | 2898.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2.300 137.95 |  |  |  |
|  |  |  |  | 229.1 | 2.581 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 32.89 1103.2 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.058 | 149.39 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | 2.920 2727.3 |  |  |  |  |  |  |
|  | 9.500 | 537.23 |  |  |  |  |  |  |  |  |  |  |  | 35.68 | 21.45 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | 134.4 2.084 |  |  |  |  |  |  |
|  | 127.8 | 27.01 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 2.803 | 2727.3 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 133.9 | 2.084 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 11.000 | 150.96 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 35.82 | 21.45 |  |  |  |
| 2.803 380.72 | 10.000 | 356.20 |  |  |  |  |  |  | 0.678 2529.7 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | 2.000 125.84 |  |  |  |  |  |  |
| 90.86 2.084 | 84.89 | 27.01 |  |  |  |  |  |  | 89.11 2.17 | 9 |  |  |  |  |  |  |  |  |
|  |  |  |  | 0.651 | 2529.7 |  |  |  |  |  |  | 30.00 0.055 |  |  |  |  |  |  |
|  |  |  |  | 88.05 | 2.179 |  |  |  |  |  |  | Make-up water |  |  | 9.000 126.48 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 30.00 5.556 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Return water from process |  |  |  |
|  |  |  |  | 0.651 | 173.56 |  |  |  |  |  |  |  |  |  | FOR CONSTRUCTION |  |  |  |
| 10.500 150.12 41.45 4.263 |  |  |  |  |  |  |  |  |  |  |  |  |  | Hom 5.12.11,Rev4 |  | E O IP SL P SU | HEAT BALANCE DIAGRAM | 12 |
| 35.63 27.01 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| p [bar] h [kJ/kg] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LP: 20t/h Process - CW=25°C |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | SIEMENS AG Energy Sector |  |  |  |  |
| t [°C] m [kg/s] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | an | 6 |
| C:\D3.kgr |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  | K III , IV |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | B |  | 128.00 3432.4 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5782-5798, 5807-5816/DZ1 |  |  |  |
|  |  |  | DP = 2.000 bar |  |  |  |  | 535.0 33.27 |  |  |  |  |  |  |  |  |  |
| 130.00 3438.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | DT = 3.00 C |  |  |  |  |  |  |  |  |  |  | Output at exit flange gearbox = 26255 kW |  |  |  |
| 538.0 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | A |  |  | 128.00 | 3432.4 |  | 128.00 3432.4 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 535.0 | 0.100 |  | 535.0 33.17 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Sealing | steam |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | G 25840 kW |  |  |  |
| --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 159.00 | 1029.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 237.8 | 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | B |  |  |  |
|  |  |  |  | 33.425 3163.4 |  |  |  |  |  | 34.817 | 3163.4 |  |  |  |  |  |  |
|  |  |  |  | 372.5 2.132 |  |  |  |  |  | 373.7 | 2.132 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 0.054 | 2273.0 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 34.42 | 14.23 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 19.084 3024.5 |  |  |  |  |  |  |
| 33.425 902.80 | 159.50 | 884.58 |  |  |  |  |  |  |  |  |  |  |  | C |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 298.6 1.60 | 9 |  |  |  |  |  |
| 211.0 2.132 | 205.9 | 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 18.321 3024.5 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 297.7 1.609 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 10.000 2898.0 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 230.1 8.333 A |  |  |  |
|  | 160.00 | 768.86 |  |  |  |  |  |  |  |  |  |  |  | to Process |  |  |  |
|  |  |  |  | --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 179.5 | 33.33 |  |  |  |  |  | C |  |  |  |  |  |  |  |  |  |
|  |  |  |  | --- --- |  |  |  |  |  |  | 10.000 | 2898.0 | 0.054 | 2273.0 128.00 3432.4 |  |  |  |
| 18.321 784.44 |  |  |  |  |  |  |  |  |  |  | 230.1 | 2.863 | 34.42 | 14.23 535.0 0.060 |  |  |  |
| 184.7 3.742 |  |  |  |  |  |  |  |  |  |  |  |  |  | SJAE |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 9.250 | 747.79 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 176.5 | 33.33 |  |  |  |  |  |  |  |  |  |  |  | 3.000 105.04 |  |  |  |
|  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 25.00 1103.2 |  |  |  |
|  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 9.500 2898.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2.300 132.70 |  |  |  |
|  |  |  |  | 229.1 2.863 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 31.64 1103.2 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 0.054 | 144.14 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 2.453 2722.9 |  |  |  |  |  |  |
|  | 9.500 | 512.32 |  |  |  |  |  |  |  |  |  |  | 34.42 | 18.40 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 130.2 1.985 |  |  |  |  |  |  |
|  | 121.9 | 26.73 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 2.355 2722.9 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 129.8 1.985 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 11.000 | 145.71 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 34.56 | 18.40 |  |  |  |
| 2.355 360.97 | 10.000 | 336.95 |  |  |  |  |  | 0.564 2528.1 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 2.000 125.84 |  |  |  |  |  |  |
| 86.17 1.985 | 80.30 | 26.73 |  |  |  |  |  | 84.39 2.02 | 0 |  |  |  |  |  |  |  |  |
|  |  |  |  | 0.542 2528.1 |  |  |  |  |  |  | 30.00 0.055 |  |  |  |  |  |  |
|  |  |  |  | 83.36 2.020 |  |  |  |  |  |  | Make-up water |  |  | 9.000 126.48 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 30.00 8.333 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | Return water from process |  |  |  |
|  |  |  |  | 0.542 165.89 |  |  |  |  |  |  |  |  |  | FOR CONSTRUCTION |  |  |  |
| 10.500 143.95 39.62 4.004 |  |  |  |  |  |  |  |  |  |  |  |  | Hom 5.12.11,Rev4 |  | E O IP SL P SU | HEAT BALANCE DIAGRAM | 12 |
| 34.15 26.73 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| p [bar] h [kJ/kg] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LP: 30t/h Process - CW=25°C |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SIEMENS AG Energy Sector |  |  |  |  |
| t [°C] m [kg/s] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | K | 7 |
| C:\D.kgr |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  | K III , IV |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | B |  | 128.00 3432.4 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5782-5798, 5807-5816/DZ1 |  |  |  |
|  |  |  | DP = 2.000 bar |  |  |  |  | 535.0 33.27 |  |  |  |  |  |  |  |  |  |
| 130.00 3438.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | DT = 3.00 C |  |  |  |  |  |  |  |  |  |  | Output at exit flange gearbox = 24308 kW |  |  |  |
| 538.0 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | A |  |  | 128.00 | 3432.4 |  | 128.00 3432.4 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 535.0 | 0.100 |  | 535.0 33.17 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Sealing | steam |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | G 23920 kW |  |  |  |
| --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 159.00 | 1029.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 237.8 | 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | B |  |  |  |
|  |  |  |  | 33.425 3163.4 |  |  |  |  |  | 34.817 | 3163.4 |  |  |  |  |  |  |
|  |  |  |  | 372.5 2.132 |  |  |  |  |  | 373.7 | 2.132 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 0.051 | 2285.5 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 33.18 | 11.45 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 19.084 3024.5 |  |  |  |  |  |  |
| 33.425 902.80 | 159.50 | 884.58 |  |  |  |  |  |  |  |  |  |  |  | C |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 298.6 1.60 | 9 |  |  |  |  |  |
| 211.0 2.132 | 205.9 | 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 18.321 3024.5 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 297.7 1.609 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 10.000 2898.0 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 230.1 11.11 A |  |  |  |
|  | 160.00 | 768.86 |  |  |  |  |  |  |  |  |  |  |  | to Process |  |  |  |
|  |  |  |  | --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 179.5 | 33.33 |  |  |  |  |  | C |  |  |  |  |  |  |  |  |  |
|  |  |  |  | --- --- |  |  |  |  |  |  | 10.000 | 2898.0 | 0.051 | 2285.5 128.00 3432.4 |  |  |  |
| 18.321 784.44 |  |  |  |  |  |  |  |  |  |  | 230.1 | 3.190 | 33.18 | 11.45 535.0 0.060 |  |  |  |
| 184.7 3.742 |  |  |  |  |  |  |  |  |  |  |  |  |  | SJAE |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 9.250 | 747.79 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 176.5 | 33.33 |  |  |  |  |  |  |  |  |  |  |  | 3.000 105.04 |  |  |  |
|  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 25.00 1103.2 |  |  |  |
|  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 9.500 2898.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2.300 127.51 |  |  |  |
|  |  |  |  | 229.1 3.190 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 30.39 1103.2 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 0.051 | 138.95 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 1.981 2721.4 |  |  |  |  |  |  |
|  | 9.500 | 482.84 |  |  |  |  |  |  |  |  |  |  | 33.18 | 15.29 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 127.3 1.864 |  |  |  |  |  |  |
|  | 114.9 | 26.40 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 1.902 2721.4 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 126.9 1.864 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 11.000 | 140.52 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 33.32 | 15.29 |  |  |  |
| 1.902 337.92 | 10.000 | 314.58 |  |  |  |  |  | 0.452 2529.8 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 2.000 125.84 |  |  |  |  |  |  |
| 80.69 1.864 | 74.97 | 26.40 |  |  |  |  |  | 78.83 1.81 | 5 |  |  |  |  |  |  |  |  |
|  |  |  |  | 0.434 2529.8 |  |  |  |  |  |  | 30.00 0.055 |  |  |  |  |  |  |
|  |  |  |  | 77.84 1.815 |  |  |  |  |  |  | Make-up water |  |  | 9.000 126.48 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 30.00 11.11 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | Return water from process |  |  |  |
|  |  |  |  | 0.434 158.71 |  |  |  |  |  |  |  |  |  | FOR CONSTRUCTION |  |  |  |
| 10.500 138.89 37.90 3.679 |  |  |  |  |  |  |  |  |  |  |  |  | Hom 5.12.11,Rev4 |  | E O IP SL P SU | HEAT BALANCE DIAGRAM | 12 |
| 32.94 26.40 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| p [bar] h [kJ/kg] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LP: 40t/h Process - CW=25°C |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SIEMENS AG Energy Sector |  |  |  |  |
| t [°C] m [kg/s] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | n | 8 |
| C:\Data\3.kgr |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  | K III , IV |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | B |  | 128.00 3432.4 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5782-5798, 5807-5816/DZ1 |  |  |  |
|  |  |  | DP = 2.000 bar |  |  |  |  | 535.0 33.27 |  |  |  |  |  |  |  |  |  |
| 130.00 3438.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | DT = 3.00 C |  |  |  |  |  |  |  |  |  |  | Output at exit flange gearbox = 22313 kW |  |  |  |
| 538.0 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | A |  |  | 128.00 | 3432.4 |  | 128.00 3432.4 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 535.0 | 0.100 |  | 535.0 33.17 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Sealing | steam |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | G 21950 kW |  |  |  |
| --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 159.00 | 1029.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 237.8 | 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | B |  |  |  |
|  |  |  |  | 33.425 3163.4 |  |  |  |  |  | 34.817 | 3163.4 |  |  |  |  |  |  |
|  |  |  |  | 372.5 2.132 |  |  |  |  |  | 373.7 | 2.132 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 0.047 | 2308.9 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 31.95 | 8.693 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 19.084 3024.5 |  |  |  |  |  |  |
| 33.425 902.80 | 159.50 | 884.58 |  |  |  |  |  |  |  |  |  |  |  | C |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 298.6 1.60 | 9 |  |  |  |  |  |
| 211.0 2.132 | 205.9 | 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 18.321 3024.5 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 297.7 1.609 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 10.000 2898.0 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 230.1 13.89 A |  |  |  |
|  | 160.00 | 768.86 |  |  |  |  |  |  |  |  |  |  |  | to Process |  |  |  |
|  |  |  |  | --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 179.5 | 33.33 |  |  |  |  |  | C |  |  |  |  |  |  |  |  |  |
|  |  |  |  | --- --- |  |  |  |  |  |  | 10.000 | 2898.0 | 0.047 | 2308.9 128.00 3432.4 |  |  |  |
| 18.321 784.44 |  |  |  |  |  |  |  |  |  |  | 230.1 | 3.572 | 31.95 | 8.693 535.0 0.060 |  |  |  |
| 184.7 3.742 |  |  |  |  |  |  |  |  |  |  |  |  |  | SJAE |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 9.250 | 747.79 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 176.5 | 33.33 |  |  |  |  |  |  |  |  |  |  |  | 3.000 105.04 |  |  |  |
|  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 25.00 1103.2 |  |  |  |
|  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 9.500 2898.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2.300 122.36 |  |  |  |
|  |  |  |  | 229.1 3.572 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 29.16 1103.2 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 0.047 | 133.79 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 1.508 2720.2 |  |  |  |  |  |  |
|  | 9.500 | 447.35 |  |  |  |  |  |  |  |  |  |  | 31.94 | 12.13 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 124.4 1.723 |  |  |  |  |  |  |
|  | 106.6 | 26.02 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 1.448 2720.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 124.1 1.723 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 11.000 | 135.37 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 32.08 | 12.13 |  |  |  |
| 1.448 310.27 | 10.000 | 287.74 |  |  |  |  |  | 0.341 2534.0 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 2.000 125.84 |  |  |  |  |  |  |
| 74.11 1.723 | 68.56 | 26.02 |  |  |  |  |  | 72.09 1.55 | 4 |  |  |  |  |  |  |  |  |
|  |  |  |  | 0.327 2534.0 |  |  |  |  |  |  | 30.00 0.055 |  |  |  |  |  |  |
|  |  |  |  | 71.14 1.554 |  |  |  |  |  |  | Make-up water |  |  | 9.000 126.48 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 30.00 13.89 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | Return water from process |  |  |  |
|  |  |  |  | 0.327 151.95 |  |  |  |  |  |  |  |  |  | FOR CONSTRUCTION |  |  |  |
| 10.500 134.95 36.28 3.278 |  |  |  |  |  |  |  |  |  |  |  |  | Hom 5.12.11,Rev4 |  | E O IP SL P SU | HEAT BALANCE DIAGRAM | 12 |
| 31.99 26.02 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| p [bar] h [kJ/kg] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LP: 50t/h Process - CW=25°C |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SIEMENS AG Energy Sector |  |  |  |  |
| t [°C] m [kg/s] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | K | 9 |
| C:\Dg |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  | K III , IV |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | B |  | 128.00 3432.4 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5782-5798, 5807-5816/DZ1 |  |  |  |
|  |  |  | DP = 2.000 bar |  |  |  |  | 535.0 33.27 |  |  |  |  |  |  |  |  |  |
| 130.00 3438.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | DT = 3.00 C |  |  |  |  |  |  |  |  |  |  | Output at exit flange gearbox = 20299 kW |  |  |  |
| 538.0 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | A |  |  | 128.00 | 3432.4 |  | 128.00 3432.4 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 535.0 | 0.100 |  | 535.0 33.17 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Sealing | steam |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | G 19960 kW |  |  |  |
| --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 159.00 | 1029.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 237.8 | 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | B |  |  |  |
|  |  |  |  | 33.425 3163.4 |  |  |  |  |  | 34.817 | 3163.4 |  |  |  |  |  |  |
|  |  |  |  | 372.5 2.132 |  |  |  |  |  | 373.7 | 2.132 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 0.044 | 2357.1 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 30.72 | 5.960 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 19.084 3024.5 |  |  |  |  |  |  |
| 33.425 902.80 | 159.50 | 884.58 |  |  |  |  |  |  |  |  |  |  |  | C |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 298.6 1.60 | 9 |  |  |  |  |  |
| 211.0 2.132 | 205.9 | 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 18.321 3024.5 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 297.7 1.609 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 10.000 2898.0 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 230.1 16.67 A |  |  |  |
|  | 160.00 | 768.86 |  |  |  |  |  |  |  |  |  |  |  | to Process |  |  |  |
|  |  |  |  | --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 179.5 | 33.33 |  |  |  |  |  | C |  |  |  |  |  |  |  |  |  |
|  |  |  |  | --- --- |  |  |  |  |  |  | 10.000 | 2898.0 | 0.044 | 2357.1 128.00 3432.4 |  |  |  |
| 18.321 784.44 |  |  |  |  |  |  |  |  |  |  | 230.1 | 4.047 | 30.72 | 5.960 535.0 0.060 |  |  |  |
| 184.7 3.742 |  |  |  |  |  |  |  |  |  |  |  |  |  | SJAE |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 9.250 | 747.79 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 176.5 | 33.33 |  |  |  |  |  |  |  |  |  |  |  | 3.000 105.04 |  |  |  |
|  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 25.00 1103.2 |  |  |  |
|  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 9.500 2898.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2.300 117.25 |  |  |  |
|  |  |  |  | 229.1 4.047 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 27.94 1103.2 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 0.044 | 128.68 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 1.035 2720.0 |  |  |  |  |  |  |
|  | 9.500 | 401.72 |  |  |  |  |  |  |  |  |  |  | 30.72 | 8.877 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 121.9 1.545 |  |  |  |  |  |  |
|  | 95.73 | 25.54 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 0.994 2720.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 121.7 1.545 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 11.000 | 130.25 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 30.86 | 8.877 |  |  |  |
| 0.994 275.23 | 10.000 | 253.83 |  |  |  |  |  | 0.234 2544.8 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 2.000 125.84 |  |  |  |  |  |  |
| 65.75 1.545 | 60.46 | 25.54 |  |  |  |  |  | 63.48 1.21 | 2 |  |  |  |  |  |  |  |  |
|  |  |  |  | 0.224 2544.8 |  |  |  |  |  |  | 30.00 0.055 |  |  |  |  |  |  |
|  |  |  |  | 62.58 1.212 |  |  |  |  |  |  | Make-up water |  |  | 9.000 126.48 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | 30.00 16.67 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | Return water from process |  |  |  |
|  |  |  |  | 0.224 145.32 |  |  |  |  |  |  |  |  |  | FOR CONSTRUCTION |  |  |  |
| 10.500 132.16 34.70 2.757 |  |  |  |  |  |  |  |  |  |  |  |  | Hom 5.12.11,Rev4 |  | E O IP SL P SU | HEAT BALANCE DIAGRAM | 12 |
| 31.33 25.54 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| p [bar] h [kJ/kg] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LP: 60t/h Process - CW=25°C |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SIEMENS AG Energy Sector |  |  |  |  |
| t [°C] m [kg/s] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | K | 10 |
| C:\gr |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  | Guaranteed Operation Conditions K III , IV |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | B |  | 128.00 3432.4 |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 5782-5798, 5807-5816/DZ1 |  |  |  |
|  |  |  | DP = 2.000 bar |  |  |  |  | 535.0 33.27 |  |  |  |  |  |  |  |  |
| 130.00 3438.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | DT = 3.00 C |  |  |  |  |  |  |  |  |  | Output at exit flange gearbox = 18308 kW |  |  |  |
| 538.0 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | A |  |  | 128.00 | 3432.4 |  | 128.00 3432.4 |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 535.0 | 0.100 |  | 535.0 33.17 |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Sealing | steam |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | G 17990 kW |  |  |  |
| --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 159.00 | 1029.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 237.8 | 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | B |  |  |  |
|  |  |  |  | 33.425 3163.4 |  |  |  |  |  | 34.817 | 3163.4 |  |  |  |  |  |
|  |  |  |  | 372.5 2.132 |  |  |  |  |  | 373.7 | 2.132 |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 0.041 2457.0 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 29.49 3.264 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 19.084 3024.5 |  |  |  |  |  |
| 33.425 902.80 | 159.50 | 884.58 |  |  |  |  |  |  |  |  |  |  | C |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 298.6 1.60 | 9 |  |  |  |  |
| 211.0 2.132 | 205.9 | 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 18.321 3024.5 |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 297.7 1.609 |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 10.000 2898.0 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 230.1 19.44 A |  |  |  |
|  | 160.00 | 768.86 |  |  |  |  |  |  |  |  |  |  | to Process |  |  |  |
|  |  |  |  | --- --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 179.5 | 33.33 |  |  |  |  |  | C |  |  |  |  |  |  |  |  |
|  |  |  |  | --- --- |  |  |  |  |  |  | 10.000 | 2898.0 | 0.041 2457.0 128.00 3432.4 |  |  |  |
| 18.321 784.43 |  |  |  |  |  |  |  |  |  |  | 230.1 | 4.738 | 29.49 3.264 535.0 0.060 |  |  |  |
| 184.7 3.742 |  |  |  |  |  |  |  |  |  |  |  |  | SJAE |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |
|  | 9.250 | 747.79 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |
|  | 176.5 | 33.33 |  |  |  |  |  |  |  |  |  |  | 3.000 105.04 |  |  |  |
|  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 25.00 1103.2 |  |  |  |
|  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |
|  |  |  |  | 9.500 2898.0 |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 2.300 112.10 |  |  |  |
|  |  |  |  | 229.1 4.738 |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 26.71 1103.2 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 0.041 123.53 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 0.551 2715.9 |  |  |  |  |  |
|  | 9.500 | 332.33 |  |  |  |  |  |  |  |  |  |  | 29.49 5.409 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 117.4 1.269 |  |  |  |  |  |
|  | 79.21 | 24.85 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 0.529 2715.9 |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 117.2 1.269 |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 11.000 125.11 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 29.63 5.409 |  |  |  |
| 0.529 224.32 | 10.000 | 205.13 |  |  |  |  |  | 0.129 2572.5 |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 2.000 125.84 |  |  |  |  |  |
| 53.60 1.269 | 48.81 | 24.85 |  |  |  |  |  | 50.98 0.71 | 6 |  |  |  |  |  |  |  |
|  |  |  |  | 0.124 2572.5 |  |  |  |  |  |  | 30.00 0.055 |  |  |  |  |  |
|  |  |  |  | 50.15 0.716 |  |  |  |  |  |  | Make-up water |  | 9.000 126.48 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 30.00 19.44 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | Return water from process |  |  |  |
|  |  |  |  | 0.124 137.96 |  |  |  |  |  |  |  |  | FOR CONSTRUCTION |  |  |  |
| 10.500 130.57 32.94 1.985 |  |  |  |  |  |  |  |  |  |  |  |  | Hom 5.12.11,Rev4 | E O IP SL P SU | HEAT BALANCE DIAGRAM | 12 |
| 30.95 24.85 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| p [bar] h [kJ/kg] |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LP: 70t/h Process - CW=25°C |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | SIEMENS AG Energy Sector |  |  |  |
| t [°C] m [kg/s] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Kn | 11 |
| C:\r |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  |  |  |  |  |  |  |  |  |  |  |  | Guaranteed Operation Conditions K III , IV |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | B |  | 128.00 3432.4 |  |  |  |  | Rev.4 |  |  |  |  |
|  |  |  | DP = 2.000 bar |  |  |  |  | 535.0 33.27 |  |  |  |  |  |  |  |  |  |
| 130.00 3438.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | DT = 3.00 C |  |  |  |  |  |  |  |  |  | Output at exit flange gearbox = 31250 kW |  |  |  |  |
| 538.0 33.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | A |  |  | 128.00 | 3432.4 |  | 128.00 3432.4 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 535.0 | 0.100 |  | 535.0 33.17 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Sealing steam |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | G 30750 kW |  |  |  |  |
| 159.00 1646.6 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 159.00 | 1027.6 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 346.8 1.000 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 237.5 | 34.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | B |  |  |  |  |
|  |  |  |  | 33.352 3162.9 |  |  |  |  |  | 34.742 | 3162.9 |  |  |  |  |  |  |
|  |  |  |  | 372.3 2.189 |  |  |  |  |  | 373.4 | 2.189 |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 0.102 2287.6 |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 46.20 22.73 |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 19.039 3024.1 |  |  |  |  |  |  |
| 33.352 902.12 | 159.50 | 883.50 |  |  |  |  |  |  |  |  |  |  | C |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 298.4 1.64 | 3 |  |  |  |  |  |
| 210.9 2.189 | 205.6 | 34.33 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 18.278 3024.1 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 297.5 1.643 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- A |  |  |  |  |
|  | 160.00 | 768.86 |  |  |  |  |  |  |  |  |  |  | to Process |  |  |  |  |
|  |  |  |  | --- --- |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 179.5 | 34.33 |  |  |  |  |  | C |  |  |  |  |  |  |  |  |  |
|  |  |  |  | --- --- |  |  |  |  |  |  | 10.000 | 2897.9 | 0.102 2287.6 128.00 3432.4 |  |  |  |  |
| 18.278 784.60 |  |  |  |  |  |  |  |  |  |  | 230.1 | 2.163 | 46.20 22.73 535.0 0.060 |  |  |  |  |
| 184.8 3.832 |  |  |  |  |  |  |  |  |  |  |  |  | SJAE |  |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 9.250 | 747.79 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 176.5 | 34.33 |  |  |  |  |  |  |  |  |  |  | 3.000 138.47 |  |  |  |  |
|  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 33.00 1150.0 |  |  |  |  |
|  |  |  |  |  |  |  | --- | --- |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 9.500 2897.9 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 2.300 180.01 |  |  |  |  |
|  |  |  |  | 229.1 2.163 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 42.96 1150.0 |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 0.102 193.37 |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 3.841 2735.1 |  |  |  |  |  |  |
|  | 9.500 | 578.70 |  |  |  |  |  |  |  |  |  |  | 46.20 28.34 |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 142.2 2.285 |  |  |  |  |  |  |
|  | 137.5 | 28.34 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 3.688 2735.1 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 141.2 2.285 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 11.000 194.94 |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 46.35 28.34 |  |  |  |  |
| 3.688 416.87 | 10.000 | 391.76 |  |  |  |  |  | 0.915 2536. | 9 |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 2.000 125.84 |  |  |  |  |  |  |
| 99.43 2.285 | 93.35 | 28.34 |  |  |  |  |  | 97.17 2.163 |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 0.878 2536.9 |  |  |  |  |  |  | 30.00 1.055 |  |  |  |  |  |  |
|  |  |  |  | 96.05 2.163 |  |  |  |  |  |  | Make-up water |  | --- --- |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | --- --- |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | Return water from process |  |  |  |  |
|  |  |  |  | 0.878 219.20 |  |  |  |  |  |  |  |  | FOR CONSTRUCTION |  |  |  |  |
| 10.500 198.90 52.36 4.448 |  |  |  |  |  |  |  |  |  |  |  |  |  | Hom 5.12.11,Rev4 | E O IP SL P SU | HEAT BALANCE DIAGRAM | 12 |
| 47.31 28.34 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| p [bar] h [kJ/kg] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | LP: TRL - CW=33°C |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | SIEMENS AG Energy Sector |  |  |  |
| t [°C] m [kg/s] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | K | 12 |
| C:\Data.kgr |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |